CMGT 235 – Mechanical and Electrical Systems

|  |  |
| --- | --- |
| Homework #3 | Due: 9/1 |

**Show all work for full credit.**

20 pts total

**Name**: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

1. Calculate the rate of heat loss due to transmission, infiltration, and ventilation for a 96 ft x 100 ft. single story office building. The ceiling height is 12 feet, and the maximum occupancy is 80 people. The ACH = 6.0. The required ventilation rate per person is 15 CFM. Inside temperature is 72°F and the outside temperature is 45°F. Use 3-decimals for all U-factors. Neglect the heat loss due to the flat roof.
**Round all calculations for q to whole numbers. Show all calculations for full credit.**

Complete the following:
2. **Heat Loss Due to Transmission**

|  |  |
| --- | --- |
| Specifications | Calculate the U-Factor (3-decimals) |
| Walls R-19 (6” insulation) |  |
| Ceilings R-30 (10” insulation) |  |
| Windows R-3.13 |  |
| Doors R-3.70 |  |

Floor SOG (2 in thick edge insulation, R=5)

Gross Wall Area = 2 x 96 ft x 12 ft + 2 x 100 ft x 12 ft = 2304 ft2 + 2400 ft2 = 4704 ft2

Window Area = 1600 ft2

Door Area = 320 ft2

Ceiling Area = 9600 ft2

Calculate the Net Wall Area = \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

qtransmission = U x A x ∆T

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Building Element | U-Factor | Area (ft2) | ∆T (°F) | q (BTUH) |
| Walls |  |  |  |  |
| Windows |  |  |  |  |
| Doors |  |  |  |  |
| Ceiling |  |  |  |  |
| Slab = Uf x L |  |  |
| Total Heat Loss Due to Transmission |  |

Continued on Back

1. **Heat Loss Due to Infiltration**

qinfililtration = C x ACH x V x ∆T

1. **Heat Loss Due to Ventilation**

qventilation = 1.1 x Qairflow x ∆T

1. Calculate the Total Rate of Heat Loss for the Office Building

|  |  |
| --- | --- |
| qtransmission |  |
| qinfililtration |  |
| qventilation |  |
| qtotal  |  |