CMGT 235 – Electrical and Mechanical Systems

Solution #1

In Class Activity #1 – Heat Load Calculation for a Small Building

Name: ________________________________________________________________

Name: ________________________________________________________________

Name: ________________________________________________________________

R-Value Table

| Building Component | R-Value |
| --- | --- |
| Wildebeest snout siding | 0.81 |
| Weevil Hide sheathing | 0.98 |
| Wookie fiber insulation | 3.78 per inch of thickness |
| Wombat Fur insulation | 3.70 per inch of thickness |
| Wabbit foot wallboard | 16.80 per inch of thickness |
| 2x4 Wood Stub | 4.38 |
| Walleye Scales | 0.78 |
| Walrus Tusk | 0.33 |
| Windows per/sf | 2.30 |
| Doors | 5.60 |
| Inside Air Film | 0.68 |
| Outside Air Film | 0.17 |
| Air space | 0.72 per inch of thickness |

- Determine the R-Value and U-Factor for the Wall:

- Wall Assembly (At Framing)

| Wall R Value | R-Value |  | Total R-Value |
| --- | --- | --- | --- |
| Outside Air Film | 0.17 |  | 0.17 |
| Wildebeest Snout Siding | 0.81 |  | 0.81 |
| Weevil Hide Sheathing | 0.98 |  | 0.98 |
| 2x4 Wood Stud | 4.38 |  | 4.38 |
| 1/2" Wabbit Foot Wallboard | 16.80 | per/in | 8.40 |
| Inside Air Film | 0.68 |  | 0.68 |
| Total R |  |  | 15.42 |
| U-Factor (use three decimals) |  |  | 0.065 |

- Wall Assembly (At Insulation)

| Wall R Value | R-Value |  | Total R-Value |
| --- | --- | --- | --- |
| Outside air film value | 0.17 |  | 0.17 |
| Wildebeest snout siding | 0.81 |  | 0.81 |
| Weevil Hide sheathing | 0.98 |  | 0.98 |
| 3-1/2” Wookie fiber insulation | 3.78 | per/in | 13.23 |
| 1/2" Wabbit foot wallboard | 16.80 | per/in | 8.40 |
| Inside air film value | 0.68 |  | 0.68 |
| Total R |  |  | 24.27 |
| U-Factor (use three decimals) |  |  | 0.041 |

- Determine the average U-Factor for the wall assembly. SHOW ALL WORK

1/2" wabbit's foot wallboard

2 x 4 studs (8 in. on Center)

Wookie fiber insulation

Weevil hide sheathing

Wildebeest snout siding with single layer building paper

Wall Assembly

Hint: Determine the percentage of wall that is 2x4 stud and the percentage that is insulated.

U-Factor Average = 0.065 x (1.5/8) + 0.041 x (6.5/8) = 0.065 x 0.1875 + 0.041 x 0.8125 = 0.045

- Ceiling Assembly

| Ceiling R Value | R-Value |  | Total R-Value |
| --- | --- | --- | --- |
| 18″ Wombat fur | 3.70 | per/in | 66.60 |
| 1/2" Wabbit foot wallboard | 16.80 | per/in | 8.40 |
| 10″ air space | 0.72 | per/in | 7.20 |
| Inside air film value | 0.68 |  | 0.68 |
| Outside air film value | 0.17 |  | 0.17 |
| Total R |  |  | 83.05 |
| U-Factor (use three decimals) |  |  | 0.012 |

160 ft

100 ft

Building Construction Data

- Calculate Building Volume

Building Dimensions

| Length (ft) | 160 |
| --- | --- |
| Width (ft) | 100 |
| Ceiling Height (ft) | 15 |
| Volume per floor (ft3) = | 240,000 |
| Total Building Volume (ft3) = | 720,000 |

- Calculate Wall, Window, and Door Area

Wall Schedule

| Description | Length (ft) | Height (ft) | Area (ft2) |
| --- | --- | --- | --- |
| North | 160 | 15 | 2400 |
| East | 100 | 15 | 1500 |
| South | 160 | 15 | 2400 |
| West | 100 | 15 | 1500 |
| Total |  |  | 7800 (per floor) |

Window Schedule

| Quantity | Width (ft) | Height (ft) | Area (ft2) |
| --- | --- | --- | --- |
| 30 | 8 | 6 | 1440 |
| Total |  |  | 1440 (per floor |

Door Schedule

| Quantity | Width (ft) | Height (ft) | Area (ft2) |
| --- | --- | --- | --- |
| 8 | 4 | 8 | 256 |
| 4 | 4 | 10 | 160 |
| Total |  |  | 416 |

- Calculate Net Wall Area

Net Wall Area = Total Wall Area – Total Window Area – Total Door Area

Net Wall Area = 23,400 – 4,320 – 416 = 18,664 ft2

- HEAT LOAD CALCULATION

- Heat Loss Due to Infiltration

Method 1

|  | Convection: BTUH heat gain/loss due to infiltration qinfil = C x ACH x V x ∆T |  |  |
| --- | --- | --- | --- |
|  | C = | 0.018 Btu/ft3 |  |
|  | ACH = | 3.0 |  |
|  | V = | 720,000 ft3 |  |
|  | ∆T = | 42 °F |  |
| (Round q to Whole Number) | qinfil = | 1,632,960 | BTUH |

Method 2 (check of Method 1)

Step 1: Find cfm

|  | CFM = (ACH x V) / 60 |  |  |
| --- | --- | --- | --- |
|  | ACH = | 3.0 |  |
|  | V = | 720,000 ft3 |  |
|  | time | 60 min/hr |  |
|  | CFM = | 36,000 |  |

|  | BTUH = CFM x 1.08 x ∆T |  |  |
| --- | --- | --- | --- |
| Step 2: Insert step 1 cfm | CFM = | 36,000 |  |
|  | 1.08 |  |  |
|  | ∆T = | 42 °F |  |
|  | BTUH = | 1,632,9600 |  |

- Heat Loss Due to Ventilation

|  | Convection: BTUH heat/gain loss due to ventilation qventilation = 1.08 x cfm total vent. x ∆T Heating Coil |  |  |  |
| --- | --- | --- | --- | --- |
|  |  | Number of | CFM |  |
|  | 15 CFM/Wallaby X | 80 = | 1200 CFM |  |
|  | 5 CFM/Weasels X | 900 = | 4500 CFM |  |
|  |  |  | 5700 | CFM total ventilation |
|  | CFM total ventilation | 5700 |  |  |
|  | ∆T = | 47 °F |  |  |
| (Round q to Whole Number) | qventilation | 289,332 BTUH |  |  |

- Design Conditions

| Infiltration Data |  |  | Winter Design Criteria |  |
| --- | --- | --- | --- | --- |
| Building Volume | 720,000 |  | Mixed Air Temp | 55 ⁰F |
| Air Changes/Hour | 3.0 |  | Return Air Temp | 62 ⁰F |
| Infiltration CFM | 36,000 |  | Outside Temp | 36 ⁰F |
|  |  |  | Supply Air Temp | 108 ⁰F |
|  |  |  | Daytime Setpoint | 78 ⁰F |
|  |  |  | Design ΔT | 42 ⁰F |
|  |  |  | Heating Coil Air ΔT | 47 ⁰F |
|  |  |  | Heating Coil Water ΔT | 27 ⁰F |

- Heat Loss Due to Transmission (Round q to Whole Number)

| Component | U-Factor (Btu/h x ft2 x ⁰F) | Area (ft2) | ΔT (⁰F) | qTransmission = U x A x ΔT (BTUH) |
| --- | --- | --- | --- | --- |
| Walls (Net) | 0.045 | 18,664 | 42 | 35,275 |
| Windows | 0.435 | 4,320 | 42 | 78,926 |
| Doors | 0.179 | 416 | 42 | 3,127 |
| Ceiling | 0.012 | 16,000 | 42 | 8,064 |
| Total Envelope Heat Loss Due to Transmission |  |  |  | 125,392 |

- Heat Loss Due to Convection (From Page 5)

| qInfiltration (BTUH) | 1,632,960 |
| --- | --- |
| qVentilation (BTUH) | 289,332 |

- Total Building Heat Load (qtotal = qTransmission + qInfiltration + qVentilation)

| Total Heat Coil Load (BTUH) | 2,047,685 |
| --- | --- |

Extra Credit

- FAN AND PUMP DATA

- CFM Req. to move across heating coil = [Total Space Heat Loss/Gain / Heating coil air ∆T] * 1.08

= (2,047,685/ 47) x 1.08 = 47,053 CFM

- GPM Req. to flow through heating coil = Total Coil Load / (Heating coil water ∆T * 500)

= 2,047,685/ (27 x 500) = 152 GPM