CMGT 235 – Electrical and Mechanical Systems

Department of Construction Management  California State University, Chico

Exam #2 [100 points]

You may work with one person or individually. Every student SHALL complete their own answer sheet.

Name:

Name:

- Complete the following steps for the dwelling plan provided. The owner has approved all options shown.

Step 1. Calculate the Available Water Pressure

MDSSPA = 60 psi

Highest Fixture = 10 feet above the source of supply

Meter Pressure loss = 5 psi

Water Softener Pressure Loss = 9 psi

Step 2. Determine the Effective Maximum Developed Length (DL) of Pipe

Length of pipe to the Furthest Fixture = 105 feet

Step 3. Complete the WSFU table below. [2016 CPC - Table 610.3]

Mark all fixtures shown on the plan using a yellow highlighter.

There is a total of five ½" hose bibbs: three on one supply segment and two on another supply segment.

| Water Supply Fixture Units |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Fixture | # of Fix. | HOT WSFU |  | COLD WSFU |  | TOTAL WSFU |  |
|  |  | EACH | THIS JOB | EACH | THIS JOB | EACH | THIS JOB |
| SHW |  |  |  |  |  |  |  |
| BT |  |  |  |  |  |  |  |
| BT/SHW |  |  |  |  |  |  |  |
| LAV |  |  |  |  |  |  |  |
| WC FT |  |  |  |  |  |  |  |
| KS |  |  |  |  |  |  |  |
| DW |  |  |  |  |  |  |  |
| CW |  |  |  |  |  |  |  |
| LT |  |  |  |  |  |  |  |
| HB |  |  |  |  |  |  |  |
| TOTALS |  |  |  |  |  |  |  |

Step 4. Use the 2016 CPC Table 610.4 complete the table below for your results:

2016 CPC - Table 610.4

| Pressure Range |  |
| --- | --- |
| Maximum Allowable Length |  |
| Distribution Piping | Pipe Size (inches) |
| Meter and Street Service |  |
| Building Supply |  |
| Cold Water Supply |  |
| Hot Water Supply |  |

- For the private residence shown write the individual DFU value above each fixture and determine the total DFU at the points indicated.

- For the 2-line drawing shown complete the 1-line drawing by replacing each fitting in the locations shown with its corresponding symbol found on drawing P-011 located on lorisweb.com [CMGT 235 DIS 20].

- For the residential site shown use the Rational Method to determine the peak runoff rate (gpm) and volume (gallons) for the drainage area given. The rainfall intensity is 8.0 in/hr.

- For a building in Wilmington, NC, determine the minimum size roof drain, horizontal pipe, and leader pipe for the roof shown. Use the 2016 CPC Appendix D rainfall rate with no amendments.