| CMGT 235 – Electrical and Mechanical Systems |  |  |
| --- | --- | --- |
| Discussion No. 23 | Unit 3 - Electrical Systems | Answers Fall 2022 |

Voltage Drop

Most building electrical calculations solve for current or voltage drop.

►	Current sets conductor size.

►	Excess voltage drop may require an increase in conductor size.

THHN Wire stands for - Thermoplastic High Heat-resistant Nylon coated.

THHN is UL listed with a rated 90 degrees Celsius in dry locations or 75 degrees Celsius in wet applications with a THWN rating.

Excessive voltage drop in a circuit can cause:

►	Lights to flicker or burn dimly

►	Heaters to heat poorly

►	Motors to run hotter than normal and burn out

This condition causes the load to work harder with less voltage pushing the current.

The National Electrical Code (NEC) recommends limiting the voltage drop from the breaker box to the farthest outlet for power, heating, or lighting to 3 percent of the circuit voltage. [Article 210.19 (A)]

This is done by selecting the right size of wire.

Two Primary Electrical Design Concerns

- Current Required

- Voltage Drop

Sub

Panel

SHOP

IT

Es

L

Total connected load for all the lights and equipment in the shop is 15 kW.

1 kW = 1,000 Watts

Find the current required for the shop’s electrical service at:

| Service Voltage = 120 V, 1φ | Service Voltage = 240 V, 1φ |
| --- | --- |
| 15,000 W 120 V P E I = = = 125 A NEC 310.15(B)(16) (75⁰) #1 AWG Minimum Size Conductor ________________ 0.154 Conductor Resistance _____________ (Ω/1000 ft) | 15,000 W 240 V P E I = = = 62.5 A NEC 310.15(B)(16) (75⁰) #6 AWG Minimum Size Conductor ________________ 0.491 Conductor Resistance _____________ (Ω/1000 ft) |

Kirchhoff’s Voltage Law

ΣVLoop = 0

120V – VLine – VLoad – VLine = 0

VLoad = 120V – VLine –  VLine

VDLine

RLine = (2 x Ohms per 1000 ft x L)	[Note: this is the TOTAL resistance of the line, i.e. RLine + RLine]

VDLine = IT x RLine

VLoad = 120V – VDLine

%VD = (VLoad / 120V) x 100

Example 1. Find the percentage voltage drop for the length (L) shown in the table.

Case 1: 120 V, 125 A, #1 CU – Load Power 15kW

Supply Voltage = 120 V, Load Power = 15 kW

Supply Current = 125 A

Minimum Conductor Size = #1

RLine = (2 x 0.154 Ω  x  L) / 1000

Complete the table:

| Length of Conductor (L) | RLine (Ω) | VDLine (V) | VLoad (V) | % VD |
| --- | --- | --- | --- | --- |
| 90 ft | 0.02772 | 3.465 | 117 | 2.89 |
| 120 ft | 0.03696 | 4.62 | 115 | 3.85 |
| 150 ft | 0.0462 | 5.775 | 114 | 4.81 |
| 230 ft | 0.07084 | 8.855 | 111 | 7.38 |

Case 2: 120 V, 125 A, #1/0 CU – Load Power 15kW

Supply Voltage = 120V, Load Power = 15 kW

Supply Current = 125 A

Minimum Conductor Size = #1/0 (increased wire size from #1)

RLine = (2 x 0.122 Ω  x  L) / 1000

Complete the table:

| Length of Conductor (L) | RLine (Ω) | VDLine (V) | VLoad (V) | % VD |
| --- | --- | --- | --- | --- |
| 90 ft | 0.02196 | 2.745 | 117 | 2.29 |
| 120 ft | 0.02928 | 3.66 | 116 | 3.05 |
| 150 ft | 0.0366 | 4.575 | 115 | 3.81 |
| 230 ft | 0.05612 | 7.015 | 113 | 5.85 |

Case 3: 240 V, 62.5 A, #6 CU – Load Power 15kW

Supply Voltage = 240 V, Load Power = 15 kW (Increased supply voltage)

Supply Current = 62.5 A

Minimum Conductor Size = #6

RLine = (2 x 0.491 Ω  x  L) / 1000

Complete the table:

| Length of Conductor (L) | RLine (Ω) | VDLine (V) | VLoad (V) | % VD |
| --- | --- | --- | --- | --- |
| 90 ft | 0.08838 | 5.52375 | 234 | 2.30 |
| 120 ft | 0.11784 | 7.365 | 233 | 3.07 |
| 150 ft | 0.1473 | 9.20625 | 231 | 3.84 |
| 230 ft | 0.22586 | 14.11625 | 226 | 5.88 |

Example #2

A residential electric water heater is rated at 4.5 kW and operates at 208V (single phase wiring).

- Determine the recommended Over Current Protection (Circuit Breaker amperage rating)

See Rheem Use & Care Manual

or

P = I x E

I = P / E = 4500 W / 208 V = 21.63 A

NEC 240.4

Use a 30A circuit Breaker

- Determine the copper wire size AWG based on NEC.

See Rheem Use & Care Manual

Or

Article 310

Table 310.15(B)(16)

90°C CU THHN	 - #10 AWG

Or

Article 240.4

Example #3

A current of 4 amps is flowing in a conductor that has a resistance of 2Ω per 1,000 feet. Find the voltage drop if the distance from the source to the load is 1,000 feet.

RLine

= 2 Ω

RLine

= 2 Ω

Supply Current = 4 A

RLine = 4 Ω

VDLine = 4 A x 4 Ω = 16 V

Example #4

An extension power cord made of CU #12 THWN is powering a lamp 300 feet from the source. The lamp resistance is 72 Ω and the source voltage is 120 V. Find the voltage drop across the light bulb.

From Chapter 9, Table 8 Conductor Properties

12 AWG CU

Solid		1.93 ohm/kFT

Stranded	1.98 ohm/kFT		Extension cords use stranded wire

RLine = 2 x 1.98 ohm/kFT x 300 FT = 1.188 Ω

Total Circuit Current (including resistance of the conductors)

IT = ET / RT = 120 V / (1.188 Ω + 72 Ω) = 1.64 A

ELamp = IT x RLamp = 1.64 A x 72 Ω = 118 V

Check using VDLine equation

IT = 120 V / 72 Ω = 1.67 A

VDLine = 1.67 A x [2 x 1.98 ohm/kFT x 300 Ft] = 1.98 V = 2 V

ELamp = 120 V – 2 V = 118 V