**ACME CONSTRUCTION CO**

1565 Cummins Dr., Modesto, CA 95358

Phone: 209.523.2674

Fax: 209.523.0213

Date: 9/20/2021

|  |  |  |  |
| --- | --- | --- | --- |
| **TO:** | **COMPANY:** | **FAX:** | **PHONE:** |
| Estimating | North State Electric |  | 530-519.1147 |

**Project:** Accubid Office Building

**Location:** 1010 Marauder Street

Chico, CA 95926

**Trade:** Electrical

**ADDENDUM #4**

For equipment shutdown on activation of Fire Alarm system, a 1/2” conduit with two (2) #14 conductors will be run from the Fire Alarm Control Panel to the starters for AHU-1, AHU-2 and EF-1 (3 separate runs for the FACP). These pairs of #14 to be connected to the normally closed sets of dry contacts in the FACP and will control the operation of the equipment shutdowns with selector switches in the “Auto” position.