{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Instructions","K-12 School","Large Hospitals","Small to Medium Office","Medium to Big Box Retail"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Instructions","index":0,"n_rows":34,"n_cols":8,"rows_kept":34,"cut":false,"hidden":false,"merged":[[45,2,46,4],[47,2,48,4],[2,3,12,3],[2,4,2,6],[29,3,29,5],[40,2,41,4],[42,2,43,4],[19,4,19,6],[22,4,22,6],[17,4,17,6],[27,2,27,6],[10,4,10,6]]}
[]
[]
[null,null,null,null,"Advanced Energy Design Guides\nLEED v4 EA Prerequisite Minimum Energy Performance and EA Credit Optimize Energy Performance"]
[]
[null,null,null,null,"Step 1."]
[null,null,null,null,"Enable macros."]
[null,null,null,null,"Note: This calculator is for use with Excel for Mac 2011 and Excel 2007 or later."]
[]
[null,null,null,null,"Step 2."]
[null,null,null,null,"Unit of measurement",null,"IP units"]
[null,null,null,null,"Note: This selection must match the unit of measurement chosen during project registration.  The SI units are identified by italicized parenthesis within the tables."]
[]
[null,null,null,null,"Step 3."]
[null,null,null,null,"Identify the DOE climate zone for the project",null,"Zone 1"]
[null,null,null,null,"Note: This selection will hide other zones in the tables."]
[]
[null,null,null,null,"Step 4."]
[null,null,null,null,"Complete the appropriate AEDG table for your project.  Provide detailed information about the project for each recommendation required.    \n\nWhere the table says “Comply with Standard 90.1-2010,” the project team must meet the more stringent of either Standard 90.1-2010 or the local code requirements.  List the requirements met by the project in the Project Specification column."]
[]
[null,null,null,null,"Note: Refer to the rating system language to know which recommendations from the AEDG are required for your project for the prerequisite and credit."]
[]
[null,null,null,null,"Step 5. "]
[null,null,null,null,"Upload the completed table to LEED Online.  Complete any related summary fields in the LEED credit form with the results of the table."]
[]
[]
[]
[null,null,"Assumptions"]
[null,null,"All content is taken from ASHRAE 50% Advanced Energy Design Guides."]
[]
[]
[null,null,null,null,null,null,null,"V01"]
[null,null,null,null,null,null,null,"Copyright © 2012"]
[null,null,null,null,null,null,null,"U.S. Green Building Council"]
[null,null,null,null,null,null,null,"All Rights Reserved"]

{"sheet":"K-12 School","index":1,"n_rows":106,"n_cols":12,"rows_kept":106,"cut":false,"hidden":false,"merged":[[42,1,45,1],[49,1,51,1],[52,1,54,1],[6,1,9,1],[20,1,21,1],[35,1,41,1],[10,1,14,1],[15,1,17,1],[23,1,26,1],[18,1,19,1],[30,1,33,1],[90,1,97,1],[64,1,69,1],[73,1,81,1],[58,1,60,1],[104,1,105,1],[98,1,100,1],[82,1,89,1]]}
[]
[null,"ASHRAE 50% Advanced Energy Design Guide for K-12 School Buildings"]
[]
[]
[null,"Envelope"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Roof","Insulation entirely above deck","R-20.0 (R-3.5) c.i.","R-25.0 (R-4.4) c.i.","R-25.0 (R-4.4) c.i.","R-30.0 (R-5.53) c.i.","R-30.0 (R-5.53) c.i.","R-30.0 (R-5.53) c.i.","R-30.0 (R-5.53) c.i.","R-35.0 (R-6.2) c.i."]
[null,null,"Attic and other","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-49.0 (R-8.6)","R-49.0 (R-8.6)","R-49.0 (R-8.6)","R-49.0 (R-8.6)","R-60.0 (R-10.6)"]
[null,null,"Metal building","R-10.0 + R-19.0 FC (R-1.8 + R-3.3 FC)","R-10.0 + R-19.0 FC (R-1.8 + R-3.3 FC)","R-10.0 + R-19.0 FC (R-1.8 + R-3.3 FC)","R-19.0 + R-11 Ls (R-3.3 + R-1.9 Ls)","R-19.0 + R-11 Ls (R-3.3 + R-1.9 Ls)","R-25.0 + R-11 Ls (R-4.4 + R-1.9 Ls)","R-25.0 + R-11 Ls (R-4.4 + R-1.9 Ls)","R-30.0 + R-11 Ls (R-5.3 + R-1.9 Ls)"]
[null,null,"Solar Reflectance Index (SRI)",78,78,78,"Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010"]
[null,"Walls","Mass (HC > 7 Btu/sq ft·°F (143 kJ/sq m·K))","R-5.7 (R-1.0) c.i.","R-7.6 (R-1.3) c.i.","R-11.4 (R-2.0) c.i.","R-13.3 (R- 2.3) c.i.","R-13.3 (R- 2.3) c.i.","R-13.3 (R- 2.3) c.i.","R-19.5 (R-3.4) c.i.","R-19.5 (R-3.4) c.i."]
[null,null,"Steel-framed","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-15.6 c.i. (R-2.3 + R-2.7 c.i.)","R-13.0 + R-15.6 c.i. (R-2.3 + R-2.7 c.i.)","R-13.0 + R-18.8 c.i. (R-2.3 + R-3.3 c.i.)","R-13.0 + R-18.8 c.i. (R-2.3 + R-3.3 c.i.)"]
[null,null,"Wood framed and other","R-13.0 (R-2.3)","R-13.0 + R-3.8 c.i. (R-2.3 + R-0.7 c.i.)","R-13.0 + R-3.8 c.i. (R-2.3 + R-0.7 c.i.)","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-10.0 c.i. (R-2.3 + R-1.8 c.i.)","R-13.0 + R-10.0 c.i. (R-2.3 + R-1.8 c.i.)","R-13.0 + R-12.5 c.i. (R-2.3 + R-2.2 c.i.)","R-13.0 + R-15.0 c.i. (R-2.3 + R-2.6 c.i.)"]
[null,null,"Metal building","R-0.0 + R-9.8 c.i. (R-0.0 + R-1.7 c.i.) ","R-0.0 + R-9.8 c.i. (R-0.0 + R-1.7 c.i.) ","R-0.0 + R-13.0 c.i. (R-0.0 + R-2.3 c.i.)","R-0.0 + R-19 c.i. (R-0.0 + R-3.3 c.i.)","R-0.0 + R-19 c.i. (R-0.0 + R-3.3 c.i.)","R-0.0 + R-19 c.i. (R-0.0 + R-3.3 c.i.)","R-0.0 + R-19 c.i. (R-0.0 + R-3.3 c.i.)","R-0.0 + R-22.1 c.i. (R-0.0 + R-3.9 c.i.)"]
[null,null,"Below-grade walls","Comply with Standard 90.1-2010","Comply with Standard 90.-2010","R-7.5 (R-1.3) c.i. (Comply with Std 90.1-2010 in CZ 3A)","R-7.5 (R-1.3) c.i.","R-7.5 (R-1.3) c.i.","R-7.5 (R-1.3) c.i.","R-10.0 (R-1.8) c.i.","R-15.0 (R-2.6) c.i."]
[null,"Floors","Mass","R-4.2 (R-0.7) c.i.","R-10.4 (R-1.8) c.i.","R-12.5 (R-2.2) c.i.","R-14.6 (R-2.6) c.i.","R-14.6 (R-2.6) c.i.","R-14.6 (R-2.6) c.i.","R-16.7 (R-2.9) c.i.","R-20.9 (R-3.7) c.i."]
[null,null,"Steel-framed","R-19.0 (R-3.3)","R-19.0 (R-3.3)","R-30.0 (R-5.3)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-49.0 (R-8.6)"]
[null,null,"Wood framed and other","R-19.0 (R-3.3)","R-19.0 (R-3.3)","R-30.0 (R-5.3)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-49.0 (R-8.6)"]
[null,"Slabs","Unheated","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","R-10 for 24 in. (R-1.8 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)"]
[null,null,"Heated","R-7.5 (R-1.32) c.i.","R-10 for 24 in. (R-1.8 for 610 mm)","R-15 for 24 in. (R-2.6 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)","R-20 for 48 in.  (R-3.5 for 1220 mm)","R-25 for 48 in. (R-4.4 for 1220 mm)"]
[null,"Doors","Swinging","U-0.70","U-0.70","U-0.70 (U-3.97)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)"]
[null,null,"Non-swinging","U-1.45","U-0.50","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)"]
[null,"Vestibules","At building entrance","Comply with Standard 90.1-2010*","Comply with Standard 90.1-2010*","Yes for buildings > 10,000 sq ft (930 sq m) only","Yes","Yes","Yes","Yes","Yes"]
[null,"Vertical fenestration","Thermal transmittance","Nonmetal framing = U-0.56; Metal framing = U-0.65","Nonmetal framing = U-0.45; Metal framing = U-0.64","Nonmetal framing = U-0.41 (U-2.33); Metal framing = U-0.60 (U-3.40)","Nonmetal framing = U-0.38 (U-2.16); Metal framing = U-0.44 (U-2.50)","Nonmetal framing = U-0.35 (U-1.99); Metal framing = U-0.44 (U-2.50)","Nonmetal framing = U-0.35 (U-1.99); Metal framing = U-0.44 (U-2.50)","Nonmetal framing = U-0.35 (U-1.99); Metal framing = U-0.42 (U-2.38)","Nonmetal framing = U-0.33 (U-1.87); Metal framing = U-0.34 (U-1.93)"]
[null,null,"Fenestration-to-floor-area ratio (FFR)","E or W orientation = 5% maximum; N or S orientation = 7% maximum","E or W orientation = 5% maximum; N or S orientation = 7% maximum","E or W orientation = 5% maximum; N or S orientation = 7% maximum","E or W orientation = 5% maximum; N or S orientation = 7% maximum","E or W orientation = 5% maximum; N or S orientation = 7% maximum","E or W orientation = 5% maximum; N or S orientation = 7% maximum","E or W orientation = 5% maximum; N or S orientation = 7% maximum","E or W orientation = 5% maximum; N or S orientation = 7% maximum"]
[null,null,"Solar heat gain coefficient (SHGC)","E or W orientation = 0.25; N orientation = 0.62; S orientation = 0.25 (N and S reversed in Southern Hemisphere)","E or W orientation = 0.25; N orientation = 0.62; S orientation = 0.5 (N and S reversed in Southern Hemisphere)","E or W orientation = 0.25; N orientation = 0.62; S orientation = 0.25 (N and S reversed in Southern Hemisphere)","E or W orientation = 0.40; N orientation = 0.62; S orientation = 0.75 (N and S reversed in Southern Hemisphere)","E or W orientation = 0.42; N orientation = 0.62; S orientation = 0.75 (N and S reversed in Southern Hemisphere)","E or W orientation = 0.42; N orientation = 0.62; S orientation = 0.75 (N and S reversed in Southern Hemisphere)","E or W orientation = 0.42; N orientation = 0.62; S orientation = 0.75 (N and S reversed in Southern Hemisphere)","E or W orientation = 0.45; N orientation = 0.62; S orientation = 0.75 (N and S reversed in Southern Hemisphere)"]
[null,null,"Exterior sun control","S orientation only = PF-0.5 (N in Southern Hemisphere)","S orientation only = PF-0.5 (N in Southern Hemisphere)","S orientation only = PF-0.5 (N in Southern Hemisphere)","S orientation only = PF-0.5 (N in Southern Hemisphere)","S orientation only = PF-0.5 (N in Southern Hemisphere)","S orientation only = PF-0.5 (N in Southern Hemisphere)","S orientation only = PF-0.5 (N in Southern Hemisphere)","S orientation only = PF-0.5 (N in Southern Hemisphere)"]
[]
[null,"Daylighting and Lighting"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Daylighting","Visible transmittance (VT)","See Table 5-5 for appropriate VT value","See Table 5-5 for appropriate VT value","See Table 5-5 for appropriate VT value","See Table 5-5 for appropriate VT value","See Table 5-5 for appropriate VT value","See Table 5-5 for appropriate VT value","See Table 5-5 for appropriate VT value","See Table 5-5 for appropriate VT value"]
[null,null,"Interior/exterior sun control (S orientation only)","S orientation = no glare during school hours  \n(N in Southern Hemisphere)","S orientation = no glare during school hours  \n(N in Southern Hemisphere)","S orientation = no glare during school hours  \n(N in Southern Hemisphere)","S orientation = no glare during school hours  \n(N in Southern Hemisphere)","S orientation = no glare during school hours  \n(N in Southern Hemisphere)","S orientation = no glare during school hours  \n(N in Southern Hemisphere)","S orientation = no glare during school hours  \n(N in Southern Hemisphere)","S orientation = no glare during school hours  \n(N in Southern Hemisphere)"]
[null,null,"Classroom, resource rooms, cafeteria, gym, and multipurpose rooms","Daylight 100% of floor area for 2/3 of school hours","Daylight 100% of floor area for 2/3 of school hours","Daylight 100% of floor area for 2/3 of school hours","Daylight 100% of floor area for 2/3 of school hours","Daylight 100% of floor area for 2/3 of school hours","Daylight 100% of floor area for 2/3 of school hours","Daylight 100% of floor area for 2/3 of school hours","Daylight 100% of floor area for 2/3 of school hours"]
[null,null,"Administration areas","Daylight perimeter floor area (15 ft) (4.57 m) for 2/3 of school hours","Daylight perimeter floor area (15 ft) (4.57 m) for 2/3 of school hours","Daylight perimeter floor area (15 ft) (4.57 m) for 2/3 of school hours","Daylight perimeter floor area (15 ft) (4.57 m) for 2/3 of school hours","Daylight perimeter floor area (15 ft) (4.57 m) for 2/3 of school hours","Daylight perimeter floor area (15 ft) (4.57 m) for 2/3 of school hours","Daylight perimeter floor area (15 ft) (4.57 m) for 2/3 of school hours","Daylight perimeter floor area (15 ft) (4.57 m) for 2/3 of school hours"]
[null,"Interior Finishes","Interior surface average reflectance for daylighted rooms","Ceilings = 80%; Wall surfaces = 70%","Ceilings = 80%; Wall surfaces = 70%","Ceilings = 80%; Wall surfaces = 70%","Ceilings = 80%; Wall surfaces = 70%","Ceilings = 80%; Wall surfaces = 70%","Ceilings = 80%; Wall surfaces = 70%","Ceilings = 80%; Wall surfaces = 70%","Ceilings = 80%; Wall surfaces = 70%"]
[null,"Interior Lighting","Lighting power density (LPD)","Whole building = 0.70 W/sq ft (7.53 W/sq m); Gyms, multipurpose rooms = 1.0 W/sq ft (10.76 W/sq m); Classrooms, art rooms, kitchens, libraries, media centers = 0.8 W/sq ft (8.61 W/sq m); Cafeterias, lobbies = 0.7 W/sq ft (7.53 W/sq m); Offices = 0.60 W/sq ft (6.46 W/sq m); Auditoriums, restrooms = 0.5 W/sq ft (5.38 W/sq m); Corridors, mechanical rooms = 0.4 W/sq ft (4.31 W/sq m)","Whole building = 0.70 W/sq ft (7.53 W/sq m); Gyms, multipurpose rooms = 1.0 W/sq ft (10.76 W/sq m); Classrooms, art rooms, kitchens, libraries, media centers = 0.8 W/sq ft (8.61 W/sq m); Cafeterias, lobbies = 0.7 W/sq ft (7.53 W/sq m); Offices = 0.60 W/sq ft (6.46 W/sq m); Auditoriums, restrooms = 0.5 W/sq ft (5.38 W/sq m); Corridors, mechanical rooms = 0.4 W/sq ft (4.31 W/sq m)","Whole building = 0.70 W/sq ft (7.53 W/sq m); Gyms, multipurpose rooms = 1.0 W/sq ft (10.76 W/sq m); Classrooms, art rooms, kitchens, libraries, media centers = 0.8 W/sq ft (8.61 W/sq m); Cafeterias, lobbies = 0.7 W/sq ft (7.53 W/sq m); Offices = 0.60 W/sq ft (6.46 W/sq m); Auditoriums, restrooms = 0.5 W/sq ft (5.38 W/sq m); Corridors, mechanical rooms = 0.4 W/sq ft (4.31 W/sq m)","Whole building = 0.70 W/sq ft (7.53 W/sq m); Gyms, multipurpose rooms = 1.0 W/sq ft (10.76 W/sq m); Classrooms, art rooms, kitchens, libraries, media centers = 0.8 W/sq ft (8.61 W/sq m); Cafeterias, lobbies = 0.7 W/sq ft (7.53 W/sq m); Offices = 0.60 W/sq ft (6.46 W/sq m); Auditoriums, restrooms = 0.5 W/sq ft (5.38 W/sq m); Corridors, mechanical rooms = 0.4 W/sq ft (4.31 W/sq m)","Whole building = 0.70 W/sq ft (7.53 W/sq m); Gyms, multipurpose rooms = 1.0 W/sq ft (10.76 W/sq m); Classrooms, art rooms, kitchens, libraries, media centers = 0.8 W/sq ft (8.61 W/sq m); Cafeterias, lobbies = 0.7 W/sq ft (7.53 W/sq m); Offices = 0.60 W/sq ft (6.46 W/sq m); Auditoriums, restrooms = 0.5 W/sq ft (5.38 W/sq m); Corridors, mechanical rooms = 0.4 W/sq ft (4.31 W/sq m)","Whole building = 0.70 W/sq ft (7.53 W/sq m); Gyms, multipurpose rooms = 1.0 W/sq ft (10.76 W/sq m); Classrooms, art rooms, kitchens, libraries, media centers = 0.8 W/sq ft (8.61 W/sq m); Cafeterias, lobbies = 0.7 W/sq ft (7.53 W/sq m); Offices = 0.60 W/sq ft (6.46 W/sq m); Auditoriums, restrooms = 0.5 W/sq ft (5.38 W/sq m); Corridors, mechanical rooms = 0.4 W/sq ft (4.31 W/sq m)","Whole building = 0.70 W/sq ft (7.53 W/sq m); Gyms, multipurpose rooms = 1.0 W/sq ft (10.76 W/sq m); Classrooms, art rooms, kitchens, libraries, media centers = 0.8 W/sq ft (8.61 W/sq m); Cafeterias, lobbies = 0.7 W/sq ft (7.53 W/sq m); Offices = 0.60 W/sq ft (6.46 W/sq m); Auditoriums, restrooms = 0.5 W/sq ft (5.38 W/sq m); Corridors, mechanical rooms = 0.4 W/sq ft (4.31 W/sq m)","Whole building = 0.70 W/sq ft (7.53 W/sq m); Gyms, multipurpose rooms = 1.0 W/sq ft (10.76 W/sq m); Classrooms, art rooms, kitchens, libraries, media centers = 0.8 W/sq ft (8.61 W/sq m); Cafeterias, lobbies = 0.7 W/sq ft (7.53 W/sq m); Offices = 0.60 W/sq ft (6.46 W/sq m); Auditoriums, restrooms = 0.5 W/sq ft (5.38 W/sq m); Corridors, mechanical rooms = 0.4 W/sq ft (4.31 W/sq m)"]
[null,null,"Light source lamp efficacy (mean lumens per watt)","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 ≤ 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 ≤ 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 ≤ 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 ≤ 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 ≤ 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 ≤ 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 ≤ 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 ≤ 2 ft (610 mm) = 85; All other > 50"]
[null,null,"T8 ballasts","Non-dimming = NEMA Premium Instant Start; Dimming= NEMA Premium Program Start","Non-dimming = NEMA Premium Instant Start; Dimming= NEMA Premium Program Start","Non-dimming = NEMA Premium Instant Start; Dimming= NEMA Premium Program Start","Non-dimming = NEMA Premium Instant Start; Dimming= NEMA Premium Program Start","Non-dimming = NEMA Premium Instant Start; Dimming= NEMA Premium Program Start","Non-dimming = NEMA Premium Instant Start; Dimming= NEMA Premium Program Start","Non-dimming = NEMA Premium Instant Start; Dimming= NEMA Premium Program Start","Non-dimming = NEMA Premium Instant Start; Dimming= NEMA Premium Program Start"]
[null,null,"T5/T5HO ballasts","Electronic program start","Electronic program start","Electronic program start","Electronic program start","Electronic program start","Electronic program start","Electronic program start","Electronic program start"]
[null,null,"CFL and HID ballasts","Electronic","Electronic","Electronic","Electronic","Electronic","Electronic","Electronic","Electronic"]
[null,null,"Dimming controls daylight harvesting","Dim all fixtures in daylight zones","Dim all fixtures in daylight zones","Dim all fixtures in daylight zones","Dim all fixtures in daylight zones","Dim all fixtures in daylight zones","Dim all fixtures in daylight zones","Dim all fixtures in daylight zones","Dim all fixtures in daylight zones"]
[null,null,"Lighting controls","Manual ON, auto/timed OFF in all areas as possible","Manual ON, auto/timed OFF in all areas as possible","Manual ON, auto/timed OFF in all areas as possible","Manual ON, auto/timed OFF in all areas as possible","Manual ON, auto/timed OFF in all areas as possible","Manual ON, auto/timed OFF in all areas as possible","Manual ON, auto/timed OFF in all areas as possible","Manual ON, auto/timed OFF in all areas as possible"]
[null,"Exterior Lighting","Façade and Landscape lighting","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ-3 & LZ-4; LPD = 0.05 W/sq ft (0.54 W/sq m) in LZ-2; Controls = auto OFF between 12am and 6am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ-3 & LZ-4; LPD = 0.05 W/sq ft (0.54 W/sq m) in LZ-2; Controls = auto OFF between 12am and 6am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ-3 & LZ-4; LPD = 0.05 W/sq ft (0.54 W/sq m) in LZ-2; Controls = auto OFF between 12am and 6am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ-3 & LZ-4; LPD = 0.05 W/sq ft (0.54 W/sq m) in LZ-2; Controls = auto OFF between 12am and 6am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ-3 & LZ-4; LPD = 0.05 W/sq ft (0.54 W/sq m) in LZ-2; Controls = auto OFF between 12am and 6am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ-3 & LZ-4; LPD = 0.05 W/sq ft (0.54 W/sq m) in LZ-2; Controls = auto OFF between 12am and 6am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ-3 & LZ-4; LPD = 0.05 W/sq ft (0.54 W/sq m) in LZ-2; Controls = auto OFF between 12am and 6am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ-3 & LZ-4; LPD = 0.05 W/sq ft (0.54 W/sq m) in LZ-2; Controls = auto OFF between 12am and 6am"]
[null,null,"Parking lots and drives","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)"]
[null,null,"Walkways, plazas, and special feature areas","LPD = 0.16 W/sq ft (1.72 W/sq m) in LZ-3 & LZ-4; LPD = 0.14 W/sq ft (1.51 W/sq m) in LZ-2; Controls = auto reduce to 25% (12am to 6am)","LPD = 0.16 W/sq ft (1.72 W/sq m) in LZ-3 & LZ-4; LPD = 0.14 W/sq ft (1.51 W/sq m) in LZ-2; Controls = auto reduce to 25% (12am to 6am)","LPD = 0.16 W/sq ft (1.72 W/sq m) in LZ-3 & LZ-4; LPD = 0.14 W/sq ft (1.51 W/sq m) in LZ-2; Controls = auto reduce to 25% (12am to 6am)","LPD = 0.16 W/sq ft (1.72 W/sq m) in LZ-3 & LZ-4; LPD = 0.14 W/sq ft (1.51 W/sq m) in LZ-2; Controls = auto reduce to 25% (12am to 6am)","LPD = 0.16 W/sq ft (1.72 W/sq m) in LZ-3 & LZ-4; LPD = 0.14 W/sq ft (1.51 W/sq m) in LZ-2; Controls = auto reduce to 25% (12am to 6am)","LPD = 0.16 W/sq ft (1.72 W/sq m) in LZ-3 & LZ-4; LPD = 0.14 W/sq ft (1.51 W/sq m) in LZ-2; Controls = auto reduce to 25% (12am to 6am)","LPD = 0.16 W/sq ft (1.72 W/sq m) in LZ-3 & LZ-4; LPD = 0.14 W/sq ft (1.51 W/sq m) in LZ-2; Controls = auto reduce to 25% (12am to 6am)","LPD = 0.16 W/sq ft (1.72 W/sq m) in LZ-3 & LZ-4; LPD = 0.14 W/sq ft (1.51 W/sq m) in LZ-2; Controls = auto reduce to 25% (12am to 6am)"]
[null,null,"All other exterior lighting","LPD = Comply with Standard 90.1-2010; Controls = auto reduce to 25% (12am to 6am)","LPD = Comply with Standard 90.1-2010; Controls = auto reduce to 25% (12am to 6am)","LPD = Comply with Standard 90.1-2010; Controls = auto reduce to 25% (12am to 6am)","LPD = Comply with Standard 90.1-2010; Controls = auto reduce to 25% (12am to 6am)","LPD = Comply with Standard 90.1-2010; Controls = auto reduce to 25% (12am to 6am)","LPD = Comply with Standard 90.1-2010; Controls = auto reduce to 25% (12am to 6am)","LPD = Comply with Standard 90.1-2010; Controls = auto reduce to 25% (12am to 6am)","LPD = Comply with Standard 90.1-2010; Controls = auto reduce to 25% (12am to 6am)"]
[]
[null,"Plug Loads"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Equipment Choices","Laptop computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers"]
[null,null,"ENERGY STAR equipment","All computers, equipment, and appliances","All computers, equipment, and appliances","All computers, equipment, and appliances","All computers, equipment, and appliances","All computers, equipment, and appliances","All computers, equipment, and appliances","All computers, equipment, and appliances","All computers, equipment, and appliances"]
[null,null,"Vending machines","De-lamp and specify best in class efficiency","De-lamp and specify best in class efficiency","De-lamp and specify best in class efficiency","De-lamp and specify best in class efficiency","De-lamp and specify best in class efficiency","De-lamp and specify best in class efficiency","De-lamp and specify best in class efficiency","De-lamp and specify best in class efficiency"]
[null,"Controls","Computer power control","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours"]
[null,null,"Power outlet control","Controllable power outlets with auto OFF during unoccupied hours for classrooms, office, library/media spaces.  All plug-in equipment not requiring continuous operation to use controllable outlets.","Controllable power outlets with auto OFF during unoccupied hours for classrooms, office, library/media spaces.  All plug-in equipment not requiring continuous operation to use controllable outlets.","Controllable power outlets with auto OFF during unoccupied hours for classrooms, office, library/media spaces\nAll plug-in equipment not requiring continuous operation to use controllable outlets","Controllable power outlets with auto OFF during unoccupied hours for classrooms, office, library/media spaces\nAll plug-in equipment not requiring continuous operation to use controllable outlets","Controllable power outlets with auto OFF during unoccupied hours for classrooms, office, library/media spaces.  All plug-in equipment not requiring continuous operation to use controllable outlets.","Controllable power outlets with auto OFF during unoccupied hours for classrooms, office, library/media spaces.  All plug-in equipment not requiring continuous operation to use controllable outlets.","Controllable power outlets with auto OFF during unoccupied hours for classrooms, office, library/media spaces.  All plug-in equipment not requiring continuous operation to use controllable outlets.","Controllable power outlets with auto OFF during unoccupied hours for classrooms, office, library/media spaces.  All plug-in equipment not requiring continuous operation to use controllable outlets."]
[null,null,"Policies","Implement at least one: District/school policy on allowed equipment; School energy teams","Implement at least one: District/school policy on allowed equipment; School energy teams","Implement at least one: District/school policy on allowed equipment; School energy teams","Implement at least one: District/school policy on allowed equipment; School energy teams","Implement at least one: District/school policy on allowed equipment; School energy teams","Implement at least one: District/school policy on allowed equipment; School energy teams","Implement at least one: District/school policy on allowed equipment; School energy teams","Implement at least one: District/school policy on allowed equipment; School energy teams"]
[]
[null,"Kitchen Equipment"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Kitchen Equipment","Cooking equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment"]
[null,null,"Walk-in refrigeration equipment","6 in. (150 mm) insulation on low-temp walk-in equipment, Insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, Insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, Insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, Insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, Insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, Insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, Insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, Insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser"]
[null,null,"Exhaust hoods","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand-based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand-based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand-based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand-based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand-based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand-based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand-based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand-based exhaust"]
[]
[null,"Service Water Heating"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Service Water Heating","Gas water heater (condensing)","95% efficiency","95% efficiency","95% efficiency","95% efficiency","95% efficiency","95% efficiency","95% efficiency","95% efficiency"]
[null,null,"Electric storage EF (≤12 kW, ≥20 gal (75.7 L))","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)"]
[null,null,"Point-of-use heater selection","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et"]
[null,null,"Electric heat pump water heater efficiency","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)"]
[null,null,"Solar hot-water heating","30% solar hot-water fraction when LCC effective","30% solar hot-water fraction when LCC effective","30% solar hot-water fraction when LCC effective","30% solar hot-water fraction when LCC effective","30% solar hot-water fraction when LCC effective","30% solar hot-water fraction when LCC effective","30% solar hot-water fraction when LCC effective","30% solar hot-water fraction when LCC effective"]
[null,null,"Pipe insulation (d < 1½ in. / d ≥ 1½ in.) (d < 38 mm / d ≥ 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)"]
[]
[null,"HVAC"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Ground Source Heat-Pump (GSHP) System with DOAS","GSHP cooling efficiency","17.1 EER (5.01 COP)","17.1 EER (5.01 COP)","17.1 EER (5.01 COP)","17.1 EER (5.01 COP)","17.1 EER (5.01 COP)","17.1 EER (5.01 COP)","17.1 EER (5.01 COP)","17.1 EER (5.01 COP)"]
[null,null,"GSHP heating efficiency","3.6 COP","3.6 COP","3.6 COP","3.6 COP","3.6 COP","3.6 COP","3.6 COP","3.6 COP"]
[null,null,"GSHP compressor capacity control","Two stage or variable speed","Two stage or variable speed","Two stage or variable speed","Two stage or variable speed","Two stage or variable speed","Two stage or variable speed","Two stage or variable speed","Two stage or variable speed"]
[null,null,"Water-circulation pumps","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency"]
[null,null,"Cooling tower/fluid cooler","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans"]
[null,null,"Boiler efficiency","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec"]
[null,null,"Maximum fan power","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)"]
[null,null,"Exhaust air energy recovery in DOAS","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temperature reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temperature reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temperature reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temperature reduction"]
[null,null,"DOAS ventilation control","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD"]
[null,"Fan-Coil System with DOAS","Water-cooled chiller efficiency","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010"]
[null,null,"Water circulation pumps","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency"]
[null,null,"Boiler efficiency","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec"]
[null,null,"Maximum fan power","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)"]
[null,null,"FCU fans","Multiple speed","Multiple speed","Multiple speed","Multiple speed","Multiple speed","Multiple speed","Multiple speed","Multiple speed"]
[null,null,"Economizer","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010"]
[null,null,"Exhaust air energy recovery in DOAS","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb  reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb  reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temperature reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temperature reduction"]
[null,null,"DOAS ventilation control","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD"]
[null,"VAV Air-Handling System with DOAS","Air-cooled chiller efficiency","10 EER; 12.75 IPLV (2.93 EER; 3.74 IPLV)","10 EER; 12.75 IPLV (2.93 EER; 3.74 IPLV)","10 EER; 12.75 IPLV (2.93 EER; 3.74 IPLV)","10 EER; 12.75 IPLV (2.93 EER; 3.74 IPLV)","10 EER; 12.75 IPLV (2.93 EER; 3.74 IPLV)","10 EER; 12.75 IPLV (2.93 EER; 3.74 IPLV)","10 EER; 12.75 IPLV (2.93 EER; 3.74 IPLV)","10 EER; 12.75 IPLV (2.93 EER; 3.74 IPLV)"]
[null,null,"Water-cooled chiller efficiency","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010"]
[null,null,"Water circulation pumps","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency","VFD and NEMA Premium Efficiency"]
[null,null,"Boiler efficiency","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec"]
[null,null,"Maximum fan power","0.8 W/cfm (1.69 W/L/s)","0.8 W/cfm (1.69 W/L/s)","0.8 W/cfm (1.69 W/L/s)","0.8 W/cfm (1.69 W/L/s)","0.8 W/cfm (1.69 W/L/s)","0.8 W/cfm (1.69 W/L/s)","0.8 W/cfm (1.69 W/L/s)","0.8 W/cfm (1.69 W/L/s)"]
[null,null,"Economizer","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010"]
[null,null,"Exhaust air energy recovery in DOAS","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temperature reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temperature reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temp reduction; C (marine) zones = 60% enthalpy reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temperature reduction","A (humid) zones = 60% enthalpy reduction; B (dry) zones = 60% dry-bulb temperature reduction"]
[null,null,"DOAS ventilation control","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD"]
[null,"Ducts and Dampers","Outdoor air damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper"]
[null,null,"Duct seal class","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A"]
[null,null,"Insulation level","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)"]
[]
[null,"QA"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"M&V/Benchmarking","Electrical submetering","Separately meter lighting, HVAC, general 120V, renewables, and whole building","Disaggregate submeters for lighting, HVAC, general 120V, renewables, and whole building","Disaggregate submeters for lighting, HVAC, general 120V, renewables, and whole building","Disaggregate submeters for lighting, HVAC, general 120V, renewables, and whole building","Disaggregate submeters for lighting, HVAC, general 120V, renewables, and whole building","Disaggregate submeters for lighting, HVAC, general 120V, renewables, and whole building","Disaggregate submeters for lighting, HVAC, general 120V, renewables, and whole building","Disaggregate submeters for lighting, HVAC, general 120V, renewables, and whole building"]
[null,null,"Benchmarking","Begin submetering early to address issues during warranty period; Benchmark monthly energy use; Provide training on benchmarking","Begin submetering early to address issues during warranty period; Benchmark monthly energy use; Provide training on benchmarking","Begin submetering early to address issues during warranty period; Benchmark monthly energy use; Provide training on benchmarking","Begin submetering early to address issues during warranty period; Benchmark monthly energy use; Provide training on benchmarking","Begin submetering early to address issues during warranty period; Benchmark monthly energy use; Provide training on benchmarking","Begin submetering early to address issues during warranty period; Benchmark monthly energy use\nProvide training on benchmarking","Begin submetering early to address issues during warranty period; Benchmark monthly energy use; Provide training on benchmarking","Begin submetering early to address issues during warranty period; Benchmark monthly energy use; Provide training on benchmarking"]

{"sheet":"Large Hospitals","index":2,"n_rows":112,"n_cols":12,"rows_kept":112,"cut":false,"hidden":false,"merged":[[103,1,105,1],[107,1,107,11],[109,1,111,1],[71,1,76,1],[77,1,85,1],[86,1,93,1],[94,1,102,1],[61,1,61,11],[63,1,66,1],[68,1,68,11],[44,1,46,1],[48,1,48,11],[50,1,52,1],[53,1,55,1],[56,1,58,1],[36,1,43,1],[14,1,15,1],[16,1,17,1],[18,1,19,1],[22,1,26,1],[7,1,7,11],[9,1,10,1],[11,1,13,1],[28,1,28,11],[30,1,33,1]]}
[]
[null,"ASHRAE 50% Advanced Energy Design Guide for Large Hospitals"]
[]
[]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Form/space planning","Proper zoning","Group similar space types within the building footprint","Group similar space types within the building footprint.","Group similar space types within the building footprint.","Group similar space types within the building footprint.","Group similar space types within the building footprint.","Group similar space types within the building footprint.","Group similar space types within the building footprint.","Group similar space types within the building footprint."]
[]
[null,"Envelope"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Roof","Insulation entirely above deck","R-20.0 (R-3.5) c.i.","R-25.0 (R-4.4) c.i.","R-25.0 (R-4.4) c.i.","R-30.0 (R-5.53) c.i.","R-30.0 (R-5.53) c.i.","R-30.0 (R-5.53) c.i.","R-35.0 (R-6.2) c.i.","R-35.0 (R-6.2) c.i."]
[null,null,"Solar reflectance index (SRI)",78,78,78,"Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010"]
[null,"Walls","Mass (HC > 7 Btu/sq ft·°F (143 kJ/sq m·K))","R-5.7 (R-1.0) c.i.","R-7.6 (R-1.3) c.i.","R-11.4 (R-2.0) c.i.","R-13.3 (R- 2.3) c.i.","R-13.3 (R- 2.3) c.i.","R-19.5 (R-3.4) c.i.","R-19.5 (R-3.4) c.i.","R-19.5 (R-3.4) c.i."]
[null,null,"Steel-framed","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-15.6 c.i. (R-2.3 + R-2.7 c.i.)","R-13.0 + R-18.8 c.i. (R-2.3 + R-3.3 c.i.)","R-13.0 + R-18.8 c.i. (R-2.3 + R-3.3 c.i.)","R-13.0 + R-18.8 c.i. (R-2.3 + R-3.3 c.i.)"]
[null,null,"Below-grade walls","Comply with Standard 90.1-2010","Comply with Standard 90.1-2011","R-7.5 (R-1.3) c.i. (Comply with Standard 90.1-2010 in 3A)","R-7.5 (R-1.3) c.i.","R-7.5 (R-1.3) c.i.","R-10.0 (R-1.8) c.i.","R-15.0 (R-2.6) c.i.","R-15.0 (R-2.6) c.i."]
[null,"Floors","Mass","R-4.2 (R-0.7) c.i.","R-10.4 (R-1.8) c.i.","R-12.5 (R-2.2) c.i.","R-14.6 (R-2.6) c.i.","R-14.6 (R-2.6) c.i.","R-16.7 (R-2.9) c.i.","R-20.9 (R-3.7) c.i.","R-23.0 (R-4.1) c.i."]
[null,null,"Steel-framed","R-19.0 (R-3.3)","R-19.0 (R-3.3)","R-30.0 (R-5.3)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-49.0 (R-8.6)","R-60.0 (R-10.6)"]
[null,"Slabs","Unheated","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","R-10 for 24 in. (R-1.8 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)"]
[null,null,"Heated","R-7.5 (R-1.32) for 12 in. (305 mm)","R-10.0 for 12 in. (R-1.8 for 305 mm)","R-15.0 for 24 in. (R-2.6 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)","R-20 for 48 in. (R-3.5 for 610 mm)","R-25 for 48 in. (R-4.4 for 610 mm)","R-20 (R-3.5) full slab "]
[null,"Doors","Swinging","U-0.70 (U-3.97)","U-0.70 (U-3.97)","U-0.70 (U-3.97)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)"]
[null,null,"Non-swinging","U-1.45 (U-8.23)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)"]
[null,"Vestibules","At primary visitor building entrance","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010"]
[null,"Continuous air barriers","Continuous air barriers","Entire building envelope","Entire building envelope","Entire building envelope","Entire building envelope","Entire building envelope","Entire building envelope","Entire building envelope","Entire building envelope"]
[null,"Vertical fenestration \n(full assembly—NFRC rating)","Window-to-wall ratio","40% of net wall (floor-ceiling)","40% of net wall (floor-ceiling)","40% of net wall (floor-ceiling)","40% of net wall (floor-ceiling)","40% of net wall (floor-ceiling)","40% of net wall (floor-ceiling)","40% of net wall (floor-ceiling)","40% of net wall (floor-ceiling)"]
[null,null,"Thermal transmittance","Nonmetal framing windows = 0.56; Metal framing windows = 0.65","Nonmetal framing windows = 0.45; Metal framing windows = 0.65","Nonmetal framing windows = 0.56; Metal framing windows = 0.65","Nonmetal framing windows = 0.38; Metal framing windows = 0.44","Nonmetal framing windows = 0.35; Metal framing windows = 0.42","Nonmetal framing windows = 0.35; Metal framing windows = 0.42","Nonmetal framing windows = 0.33; Metal framing windows = 0.34","Nonmetal framing windows = 0.25; Metal framing windows = 0.34"]
[null,null,"Solar heat gain coefficient (SHGC)","Nonmetal framing windows = 0.25; Metal framing windows = 0.25","Nonmetal framing windows = 0.25; Metal framing windows = 0.25","Nonmetal framing windows = 0.41; Metal framing windows = 0.6","Nonmetal framing windows = 0.26; Metal framing windows = 0.38","Nonmetal framing windows = 0.25; Metal framing windows = 0.25","Nonmetal framing windows = 0.25; Metal framing windows = 0.25","Nonmetal framing windows = 0.4; Metal framing windows = 0.4","Nonmetal framing windows = 0.4; Metal framing windows = 0.4"]
[null,null,"Light-to-solar gain ratio (LSG)","All orientations ≥ 1.5","All orientations ≥ 1.5","All orientations ≥ 1.5","All orientations ≥ 1.5","All orientations ≥ 1.5","All orientations ≥ 1.5","All orientations ≥ 1.5","All orientations ≥ 1.5"]
[null,null,"Exterior sun control","South orientation only – PF = 0.5\n(North orientation in Southern Hemisphere)","South orientation only – PF = 0.5\n(North orientation in Southern Hemisphere)","South orientation only – PF = 0.5\n(North orientation in Southern Hemisphere)","South orientation only – PF = 0.5\n(North orientation in Southern Hemisphere)","South orientation only – PF = 0.5\n(North orientation in Southern Hemisphere)","South orientation only – PF = 0.5\n(North orientation in Southern Hemisphere)","South orientation only – PF = 0.5\n(North orientation in Southern Hemisphere)","South orientation only – PF = 0.5\n(North orientation in Southern Hemisphere)"]
[]
[null,"Daylighting and Lighting"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Form-driven daylighting option","All spaces","Comply with LEED for Healthcare EQ Credit Daylight and EQ Credit Quality Views","Comply with LEED for Healthcare EQ Credit Daylight and EQ Credit Quality Views","Comply with LEED for Healthcare EQ Credit Daylight and EQ Credit Quality Views","Comply with LEED for Healthcare EQ Credit Daylight and EQ Credit Quality Views","Comply with LEED for Healthcare EQ Credit Daylight and EQ Credit Quality Views","Comply with LEED for Healthcare EQ Credit Daylight and EQ Credit Quality Views","Comply with LEED for Healthcare EQ Credit Daylight and EQ Credit Quality Views","Comply with LEED for Healthcare EQ Credit Daylight and EQ Credit Quality Views"]
[null,null,"Diagnostic and treatment block","Shape the building footprint and form such that the area within 15 ft (4.57 m) of the perimeter exceeds 40% of the floorplate.","Shape the building footprint and form such that the area within 15 ft (4.57 m) of the perimeter exceeds 40% of the floorplate.","Shape the building footprint and form such that the area within 15 ft (4.57 m) of the perimeter exceeds 40% of the floorplate.","Shape the building footprint and form such that the area within 15 ft (4.57 m) of the perimeter exceeds 40% of the floorplate.","Shape the building footprint and form such that the area within 15 ft (4.57 m) of the perimeter exceeds 40% of the floorplate.","Shape the building footprint and form such that the area within 15 ft (4.57 m) of the perimeter exceeds 40% of the floorplate.","Shape the building footprint and form such that the area within 15 ft (4.57 m) of the perimeter exceeds 40% of the floorplate.","Shape the building footprint and form such that the area within 15 ft (4.57 m) of the perimeter exceeds 40% of the floorplate."]
[null,null,"Inpatient units","Ensure that 75% of the occupied space not including patient rooms lies within 20 ft (6.10 m) of the perimeter.","Ensure that 75% of the occupied space not including patient rooms lies within 20 ft (6.10 m) of the perimeter.","Ensure that 75% of the occupied space not including patient rooms lies within 20 ft (6.10 m) of the perimeter.","Ensure that 75% of the occupied space not including patient rooms lies within 20 ft (6.10 m) of the perimeter.","Ensure that 75% of the occupied space not including patient rooms lies within 20 ft (6.10 m) of the perimeter.","Ensure that 75% of the occupied space not including patient rooms lies within 20 ft (6.10 m) of the perimeter.","Ensure that 75% of the occupied space not including patient rooms lies within 20 ft (6.10 m) of the perimeter.","Ensure that 75% of the occupied space not including patient rooms lies within 20 ft (6.10 m) of the perimeter."]
[null,null,"Staff areas (exam rooms, nurse stations, offices, corridors); public spaces (waiting, reception); and other regularly occupied spaces as applicable","Design the building form to maximize access to natural light, through sidelighting and toplighting.","Design the building form to maximize access to natural light, through sidelighting and toplighting.","Design the building form to maximize access to natural light, through sidelighting and toplighting.","Design the building form to maximize access to natural light, through sidelighting and toplighting.","Design the building form to maximize access to natural light, through sidelighting and toplighting.","Design the building form to maximize access to natural light, through sidelighting and toplighting.","Design the building form to maximize access to natural light, through sidelighting and toplighting.","Design the building form to maximize access to natural light, through sidelighting and toplighting."]
[null,"Nonform-driven daylighting option","Staff areas (exam rooms, nurse stations, offices, corridors) and public spaces (waiting, reception)","Add daylight controls to any space within 15 ft (4.57 m) of a perimeter window.","Add daylight controls to any space within 15 ft (4.57 m) of a perimeter window.","Add daylight controls to any space within 15 ft (4.57 m) of a perimeter window.","Add daylight controls to any space within 15 ft (4.57 m) of a perimeter window.","Add daylight controls to any space within 15 ft (4.57 m) of a perimeter window.","Add daylight controls to any space within 15 ft (4.57 m) of a perimeter window.","Add daylight controls to any space within 15 ft (4.57 m) of a perimeter window.","Add daylight controls to any space within 15 ft (4.57 m) of a perimeter window."]
[null,"Interior finishes","Room interior surface average reflectance","Ceilings ≥ 80%; Walls ≥ 70%","Ceilings ≥ 80%; Walls ≥ 70%","Ceilings ≥ 80%; Walls ≥ 70%","Ceilings ≥ 80%; Walls ≥ 70%","Ceilings ≥ 80%; Walls ≥ 70%","Ceilings ≥ 80%; Walls ≥ 70%","Ceilings ≥ 80%; Walls ≥ 70%","Ceilings ≥ 80%; Walls ≥ 70%"]
[null,"Interior lighting","Lighting power density (LPD)","Whole building= 0.9 W/sq ft (9.69 W/sq m); Space-by-space per Table 5-4","Whole building= 0.9 W/sq ft (9.69 W/sq m); Space-by-space per Table 5-4","Whole building= 0.9 W/sq ft (9.69 W/sq m); Space-by-space per Table 5-4","Whole building= 0.9 W/sq ft (9.69 W/sq m); Space-by-space per Table 5-4","Whole building= 0.9 W/sq ft (9.69 W/sq m); Space-by-space per Table 5-4","Whole building= 0.9 W/sq ft (9.69 W/sq m); Space-by-space per Table 5-4","Whole building= 0.9 W/sq ft (9.69 W/sq m); Space-by-space per Table 5-4","Whole building= 0.9 W/sq ft (9.69 W/sq m); Space-by-space per Table 5-4"]
[null,null,"Light source efficacy (mean lumens per watt)","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 < 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 < 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 < 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 < 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 < 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 < 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 < 2 ft (610 mm) = 85; All other > 50","T8 & T5 > 2 ft (610 mm) = 92; T8 & T5 < 2 ft (610 mm) = 85; All other > 50"]
[null,null,"Ballasts—4 ft T8 Lamps","Nondimming = NEMA Premium; Dimming= NEMA Premium Program Start","Nondimming = NEMA Premium; Dimming= NEMA Premium Program Start","Nondimming = NEMA Premium; Dimming= NEMA Premium Program Start","Nondimming = NEMA Premium; Dimming= NEMA Premium Program Start","Nondimming = NEMA Premium; Dimming= NEMA Premium Program Start","Nondimming = NEMA Premium; Dimming= NEMA Premium Program Start","Nondimming = NEMA Premium; Dimming= NEMA Premium Program Start","Nondimming = NEMA Premium; Dimming= NEMA Premium Program Start"]
[null,null,"Ballasts—Fluorescent and HID","Electronic","Electronic","Electronic","Electronic","Electronic","Electronic","Electronic","Electronic"]
[null,null,"Dimming controls daylight harvesting","Dim all fixtures in daylighted zones.","Dim all fixtures in daylighted zones.","Dim all fixtures in daylighted zones.","Dim all fixtures in daylighted zones.","Dim all fixtures in daylighted zones.","Dim all fixtures in daylighted zones.","Dim all fixtures in daylighted zones.","Dim all fixtures in daylighted zones."]
[null,null,"Lighting controls—general","Manual ON, auto/timed OFF in all areas as possible.","Manual ON, auto/timed OFF in all areas as possible.","Manual ON, auto/timed OFF in all areas as possible.","Manual ON, auto/timed OFF in all areas as possible.","Manual ON, auto/timed OFF in all areas as possible.","Manual ON, auto/timed OFF in all areas as possible.","Manual ON, auto/timed OFF in all areas as possible.","Manual ON, auto/timed OFF in all areas as possible."]
[null,null,"Surgery task lights","Use LED lights exclusively.","Use LED lights exclusively.","Use LED lights exclusively.","Use LED lights exclusively.","Use LED lights exclusively.","Use LED lights exclusively.","Use LED lights exclusively.","Use LED lights exclusively."]
[null,null,"Exit signage","0.1–0.2 W light emitting capacitor (LEC) exit signs exclusively","0.1–0.2 W light emitting capacitor (LEC) exit signs exclusively","0.1–0.2 W light emitting capacitor (LEC) exit signs exclusively","0.1–0.2 W light emitting capacitor (LEC) exit signs exclusively","0.1–0.2 W light emitting capacitor (LEC) exit signs exclusively","0.1–0.2 W light emitting capacitor (LEC) exit signs exclusively","0.1–0.2 W light emitting capacitor (LEC) exit signs exclusively","0.1–0.2 W light emitting capacitor (LEC) exit signs exclusively"]
[null,"Exterior lighting","Façade and landscape lighting","LPD = 0.15 W/sq ft (1.61 W/sq m)","LPD = 0.15 W/sq ft (1.61 W/sq m)","LPD = 0.15 W/sq ft (1.61 W/sq m)","LPD = 0.15 W/sq ft (1.61 W/sq m)","LPD = 0.15 W/sq ft (1.61 W/sq m)","LPD = 0.15 W/sq ft (1.61 W/sq m)","LPD = 0.15 W/sq ft (1.61 W/sq m)","LPD = 0.15 W/sq ft (1.61 W/sq m)"]
[null,null,"Parking lots and drives","LPD = 0.1 W/sq ft (1.08 W/sq m)","LPD = 0.1 W/sq ft (1.08 W/sq m)","LPD = 0.1 W/sq ft (1.08 W/sq m)","LPD = 0.1 W/sq ft (1.08 W/sq m)","LPD = 0.1 W/sq ft (1.08 W/sq m)","LPD = 0.1 W/sq ft (1.08 W/sq m)","LPD = 0.1 W/sq ft (1.08 W/sq m)","LPD = 0.1 W/sq ft (1.08 W/sq m)"]
[null,null,"All other exterior lighting","LPD = Comply with Standard 90.1-2010; Auto reduce to 25% (12am–6am)","LPD = Comply with Standard 90.1-2010; Auto reduce to 25% (12am–6am)","LPD = Comply with Standard 90.1-2010; Auto reduce to 25% (12am–6am)","LPD = Comply with Standard 90.1-2010; Auto reduce to 25% (12am–6am)","LPD = Comply with Standard 90.1-2010; Auto reduce to 25% (12am–6am)","LPD = Comply with Standard 90.1-2010; Auto reduce to 25% (12am–6am)","LPD = Comply with Standard 90.1-2010; Auto reduce to 25% (12am–6am)","LPD = Comply with Standard 90.1-2010; Auto reduce to 25% (12am–6am)"]
[]
[null,"PPL"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Equipment choices","Computers","Laptops = minimum 2/3 of total computers; All others = mini desktop computers","Laptops = minimum 2/3 of total computers; All others = mini desktop computers","Laptops = minimum 2/3 of total computers; All others = mini desktop computers","Laptops = minimum 2/3 of total computers; All others = mini desktop computers","Laptops = minimum 2/3 of total computers; All others = mini desktop computers","Laptops = minimum 2/3 of total computers; All others = mini desktop computers","Laptops = minimum 2/3 of total computers; All others = mini desktop computers","Laptops = minimum 2/3 of total computers; All others = mini desktop computers"]
[null,null,"ENERGY STAR equipment","All computers, equipment, appliances","All computers, equipment, appliances","All computers, equipment, appliances","All computers, equipment, appliances","All computers, equipment, appliances","All computers, equipment, appliances","All computers, equipment, appliances","All computers, equipment, appliances"]
[null,null,"Vending machines","Delamp and specify best in class efficiency.","Delamp and specify best in class efficiency.","Delamp and specify best in class efficiency.","Delamp and specify best in class efficiency.","Delamp and specify best in class efficiency.","Delamp and specify best in class efficiency.","Delamp and specify best in class efficiency.","Delamp and specify best in class efficiency."]
[null,"Controls","Computer power control","Network control with power saving modes and control during unoccupied hours or IT enterprise power management software","Network control with power saving modes and control during unoccupied hours or IT enterprise power management software","Network control with power saving modes and control during unoccupied hours or IT enterprise power management software","Network control with power saving modes and control during unoccupied hours or IT enterprise power management software","Network control with power saving modes and control during unoccupied hours or IT enterprise power management software","Network control with power saving modes and control during unoccupied hours or IT enterprise power management software","Network control with power saving modes and control during unoccupied hours or IT enterprise power management software","Network control with power saving modes and control during unoccupied hours or IT enterprise power management software"]
[null,null,"Occupancy sensors","Office plug occupancy sensors","Office plug occupancy sensors","Office plug occupancy sensors","Office plug occupancy sensors","Office plug occupancy sensors","Office plug occupancy sensors","Office plug occupancy sensors","Office plug occupancy sensors"]
[null,null,"Timer switches","Water coolers, coffee makers, small appliances = auto OFF during unoccupied hours","Water coolers, coffee makers, small appliances = auto OFF during unoccupied hours","Water coolers, coffee makers, small appliances = auto OFF during unoccupied hours","Water coolers, coffee makers, small appliances = auto OFF during unoccupied hours","Water coolers, coffee makers, small appliances = auto OFF during unoccupied hours","Water coolers, coffee makers, small appliances = auto OFF during unoccupied hours","Water coolers, coffee makers, small appliances = auto OFF during unoccupied hours","Water coolers, coffee makers, small appliances = auto OFF during unoccupied hours"]
[null,"Kitchen equipment","Cooking equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment","ENERGY STAR or California rebate-qualified equipment"]
[null,null,"Refrigeration equipment","6 in. (150 mm) insulation on low-temp walk-in equipment, insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser","6 in. (150 mm) insulation on low-temp walk-in equipment, insulated floor, LED lighting, floating-head pressure controls, liquid pressure amplifier, subcooled liquid refrigerant, evaporative condenser"]
[null,null,"Exhaust hoods","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demandbased exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demand based exhaust","Side panels, larger overhangs, rear seal at appliances, proximity hoods, VAV demandbased exhaust"]
[null,"Process loads","Elevators","Use traction elevators for all elevators, and use regenerative traction elevators for all high-use elevators.","Use traction elevators for all elevators, and use regenerative traction elevators for all high-use elevators.","Use traction elevators for all elevators, and use regenerative traction elevators for all high-use elevators.","Use traction elevators for all elevators, and use regenerative traction elevators for all high-use elevators.","Use traction elevators for all elevators, and use regenerative traction elevators for all high-use elevators.","Use traction elevators for all elevators, and use regenerative traction elevators for all high-use elevators.","Use traction elevators for all elevators, and use regenerative traction elevators for all high-use elevators.","Use traction elevators for all elevators, and use regenerative traction elevators for all high-use elevators."]
[]
[null,"Service Water Heating"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Service water heating","Gas water heater (condensing)","95% Efficiency","95% Efficiency","95% Efficiency","95% Efficiency","95% Efficiency","95% Efficiency","95% Efficiency","95% Efficiency"]
[null,null,"Point-of-use water heater","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et"]
[null,null,"Electric-heat-pump water heater","2.33 EF","2.33 EF","2.33 EF","2.33 EF","2.33 EF","2.33 EF","2.33 EF","2.33 EF"]
[null,null,"Pipe insulation (d < 1½ in. / d ≥ 1½ in.) (d < 38 mm / d ≥ 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)"]
[]
[null,"HVAC"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Heating system","No central steam; Use hot-water distribution system","Point-of-use steam for humidification and sterilization","Point-of-use steam for humidification and sterilization","Point-of-use steam for humidification and sterilization","Point-of-use steam for humidification and sterilization","Point-of-use steam for humidification and sterilization","Point-of-use steam for humidification and sterilization","Point-of-use steam for humidification and sterilization","Point-of-use steam for humidification and sterilization"]
[null,"Surgery:\nCentral air-handling \nsystem","Water-cooled chiller","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP"]
[null,null,"Water-circulation pumps","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium"]
[null,null,"Cooling towers","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans"]
[null,null,"Boiler efficiency","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec"]
[null,null,"Maximum fan power","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)"]
[null,null,"Economizer","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010","Comply with Standard 90.1-2010"]
[null,"Nonsurgery:\nWater-source heat pump (WSHP) system \nwith DOAS","WSHP part-load/full-load cooling efficiency","17.6/15.0 EER (5.16/4.40 COP)","17.6/15.0 EER (5.16/4.40 COP)","17.6/15.0 EER (5.16/4.40 COP)","17.6/15.0 EER (5.16/4.40 COP)","17.6/15.0 EER (5.16/4.40 COP)","17.6/15.0 EER (5.16/4.40 COP)","17.6/15.0 EER (5.16/4.40 COP)","17.6/15.0 EER (5.16/4.40 COP)"]
[null,null,"WSHP part-load/full-load heating efficiency","5.7/5.0 COP","5.7/5.0 COP","5.7/5.0 COP","5.7/5.0 COP","5.7/5.0 COP","5.7/5.0 COP","5.7/5.0 COP","5.7/5.0 COP"]
[null,null,"WSHP compressor capacity control","Two-speed or variable-speed","Two-speed or variable-speed","Two-speed or variable-speed","Two-speed or variable-speed","Two-speed or variable-speed","Two-speed or variable-speed","Two-speed or variable-speed","Two-speed or variable-speed"]
[null,null,"Water-circulation pumps","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium"]
[null,null,"Closed-circuit cooling tower","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans"]
[null,null,"Boiler efficiency","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec"]
[null,null,"Maximum fan power","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)"]
[null,null,"Exhaust-air energy recovery in DOAS","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness; C (marine zones) = 60% total effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness; C (marine zones) = 60% total effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","60% sensible effectiveness"]
[null,null,"DOAS ventilation control","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD"]
[null,"Nonsurgery:\nFan-coil system \nwith DOAS","Water-cooled chiller","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP"]
[null,null,"Water-circulation pumps","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium"]
[null,null,"Cooling towers","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans"]
[null,null,"Boiler efficiency","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec"]
[null,null,"Maximum fan power","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)"]
[null,null,"FCU fans","Multiple speed","Multiple speed","Multiple speed","Multiple speed","Multiple speed","Multiple speed","Multiple speed","Multiple speed"]
[null,null,"Exhaust-air energy recovery in DOAS","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness; C (marine zones) = 60% total effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness; C (marine zones) = 60% total effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","60% sensible effectiveness"]
[null,null,"DOAS ventilation control","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD"]
[null,"Nonsurgery:\nWater-source heat pump (WSHP) system \nwith DOAS","Heat recovery water-cooled chiller","4.55 COP","4.55 COP","4.55 COP","4.55 COP","4.55 COP","4.55 COP","4.55 COP","4.55 COP"]
[null,null,"Water-cooled chiller","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP","6.5 COP"]
[null,null,"Water-circulation pumps","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium","VFD and NEMA premium"]
[null,null,"Cooling towers","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans","VFD on tower fans"]
[null,null,"Boiler efficiency","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec"]
[null,null,"Maximum fan power","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)","bhp ≤ supply cfm × 0.0012 + A (kW ≤  L/s x 0.0019 + A)"]
[null,null,"Economizer","Comply with Standard 90.1-2010","Comply with Standard 90.1-2011","Comply with Standard 90.1-2012","Comply with Standard 90.1-2013","Comply with Standard 90.1-2014","Comply with Standard 90.1-2015","Comply with Standard 90.1-2016","Comply with Standard 90.1-2017"]
[null,null,"Exhaust-air energy recovery in DOAS","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness; C (marine zones) = 60% total effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness; C (marine zones) = 60% total effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","A (humid zones) = 60% total effectiveness; B (dry zones) = 60% sensible effectiveness","60% sensible effectiveness"]
[null,null,"DOAS ventilation control","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD","DCV with VFD"]
[null,"Ducts and dampers","OA damper","Motorized","Motorized","Motorized","Motorized","Motorized","Motorized","Motorized","Motorized"]
[null,null,"Duct seal class","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A"]
[null,null,"Insulation level","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)"]
[]
[null,"QA"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"M&V/Benchmarking","Electrical submeters","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heating, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heating, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heating, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heating, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heating, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heating, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heating, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heating, renewables, and whole building"]
[null,null,"Benchmarks","Benchmark monthly energy use.","Benchmark monthly energy use.","Benchmark monthly energy use.","Benchmark monthly energy use.","Benchmark monthly energy use.","Benchmark monthly energy use.","Benchmark monthly energy use.","Benchmark monthly energy use."]
[null,null,"Training","Facility operator on continuous benchmarking","Facility operator on continuous benchmarking","Facility operator on continuous benchmarking","Facility operator on continuous benchmarking","Facility operator on continuous benchmarking","Facility operator on continuous benchmarking","Facility operator on continuous benchmarking","Facility operator on continuous benchmarking"]

{"sheet":"Small to Medium Office","index":3,"n_rows":117,"n_cols":12,"rows_kept":117,"cut":false,"hidden":false,"merged":[[105,1,111,1],[112,1,116,1],[59,1,63,1],[67,1,72,1],[73,1,81,1],[82,1,90,1],[91,1,94,1],[95,1,104,1],[52,1,55,1],[6,1,9,1],[10,1,14,1],[15,1,17,1],[18,1,19,1],[20,1,21,1],[24,1,28,1],[32,1,33,1],[34,1,35,1],[36,1,41,1],[42,1,45,1],[49,1,51,1]]}
[]
[null,"ASHRAE 50% Advanced Energy Design Guide for Small to Medium Office Buildings"]
[]
[]
[null,"Envelope"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Roof","Insulation entirely above deck","R-20.0 (R-3.5) c.i.","R-25.0 (R-4.4) c.i.","R-25.0 (R-4.4) c.i.","R-30.0 (R-5.3) c.i.","R-30.0 (R-5.3) c.i.","R-30.0 (R-5.3) c.i.","R-35.0 (R-6.2) c.i.","R-35.0 (R-6.2) c.i."]
[null,null,"Attic and other","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-49.0 (R-8.6)","R-49.0 (R-8.6)","R-49.0 (R-8.6)","R-60.0 (R-10.6)","R-60.0 (R-10.6)"]
[null,null,"Metal building","R-19.0 + R-10.0 FC (R-3.3 + R-1.8 FC) ","R-19.0 + R-10.0 FC (R-3.3 + R-1.8 FC) ","R-19.0 + R-10.0 FC (R-3.3 + R-1.8 FC) ","R-19.0 + R-11.0 Ls (R-3.3 + R-1.9 Ls) ","R-19.0 + R-11.0 Ls (R-3.3 + R-1.9 Ls) ","R-19.0 + R-11.0 Ls (R-3.3 + R-1.9 Ls) ","R-30.0 + R-11.0 Ls (R-5.3 + R-1.9 Ls) ","R-30.0 + R-11.0 Ls (R-5.3 + R-1.9 Ls) "]
[null,null,"SRI",78,78,78,"No recommendation","No recommendation","No recommendation","No recommendation","No recommendation"]
[null,"Walls","Mass (HC > 7 Btu/sq ft·°F (143 kJ/sq m·K))","R-5.7 (R-1.0) c.i.","R-7.6 (R-1.3) c.i.","R-11.4 (R-2.0) c.i.","R-13.3 (R-2.3) c.i.","R-13.3 (R-2.3) c.i.","R-19.0 (R-3.3) c.i.","R-19.0 (R-3.3) c.i.","R-19.0 (R-3.3) c.i."]
[null,null,"Steel-framed","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.) ","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.) ","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.) ","R-13.0 + R-15.6 c.i. (R-2.3 + R-2.7 c.i.) ","R-13.0 + R-18.8 c.i. (R-2.3 + R-3.3 c.i.) ","R-13.0 + R-18.8 c.i. (R-2.3 + R-3.3 c.i.) ","R-13.0 + R-18.8 c.i. (R-2.3 + R-3.3 c.i.) "]
[null,null,"Wood framed and other","R-13.0 (R-2.3)","R-13.0 + R-3.8 c.i. (R-2.3 +R-0.7 c.i.)","R-13.0 + R-3.8 c.i. (R-2.3 +R-0.7 c.i.)","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.) ","R-13.0 + R-10.0 c.i. (R-2.3 + R-1.8 c.i.) ","R-13.0 + R-12.5 c.i. (R-2.3 + R-2.2 c.i.) ","R-13.0 + R-15.0 c.i. (R-2.3 + R-2.6 c.i.) ","R-13.0 + R-18.8 c.i. (R-2.3 + R-3.3 c.i.) "]
[null,null,"Metal building","R-0.0 + R-9.8 c.i. (R-0.0 + R-1.7 c.i.) ","R-0.0 + R-9.8 c.i. (R-0.0 + R-1.7 c.i.) ","R-0.0 + R-13.0 c.i. (R-0.0 + R-2.3c.i.) ","R-0.0 + R-15.8 c.i. (R-0.0 + R-2.8 c.i.) ","R-0.0 + R-19.0 c.i. (R-0.0 + R-3.3 c.i.) ","R-0.0 + R-19.0 c.i. (R-0.0 + R-3.3 c.i.) ","R-0.0 + R-22.1 c.i. (R-0.0 + R-3.9 c.i.) ","R-0.0 + R-25.0 c.i. (R-0.0 + R-4.4 c.i.) "]
[null,null,"Below-grade walls","No recommendation","No recommendation","R-7.5 (R-1.3) c.i. (No recommendation in climate zone 3A)","R-7.5 (R-1.3) c.i. ","R-7.5 (R-1.3) c.i. ","R-10.0 (R-1.8) c.i. ","R-15.0 (R-2.6) c.i. ","R-15.0 (R-2.6) c.i. "]
[null,"Floors","Mass","R-4.2 c.i. (R-0.74 c.i.)","R-10.4 (R-1.8) c.i.","R-12.5 (R-2.2) c.i.","R-14.6 (R-2.6) c.i.","R-14.6 (R-2.6) c.i.","R-16.7 (R-2.9) c.i.","R-20.9 (R-3.7) c.i.","R-20.9 (R-3.7) c.i."]
[null,null,"Steel-framed","R-19.0 (R-3.3)","R-30.0 (R-5.3)","R-30.0 (R-5.3)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-49.0 (R-8.6)","R-60.0 (R-10.6)"]
[null,null,"Wood framed and other","R-19.0 (R-3.3)","R-30.0 (R-5.3)","R-30.0 (R-5.3)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-49.0 (R-8.6)","R-60.0 (R-10.6)"]
[null,"Slabs","Unheated","No recommendation","No recommendation","No recommendation","R-15.0 (R-2.6) for 24 in. (610 mm)","R-15.0 (R-2.6) for 24 in. (610 mm)","R-20.0 (R-3.5) for 24 in. (610 mm)","R-20.0 (R-3.5) for 24 in. (610 mm)","R-20.0 (R-3.5) for 48 in. (1219 mm)"]
[null,null,"Heated","R-7.5 (R-1.32) for 12 in. (305 mm)","R-10 (R-1.8) for 24 in. (610 mm)","R-15 (R-2.6) for 24 in. (610 mm)","R-20.0 (R-3.5) for 24 in. (610 mm)","R-20.0 (R-3.5) for 24 in. (610 mm)","R-20.0 (R-3.5) for 48 in. (1219 mm)","R-25.0 (R-4.4) for 48 in. (1219 mm)","R-20.0 (R-3.5) full slab"]
[null,"Doors","Swinging","U-0.70 (U-3.97)","U-0.70 (U-3.97)","U-0.70 (U-3.97)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)"]
[null,null,"Non-swinging","U-1.45 (U-8.23)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)"]
[null,"Vestibules","At building entrance","No recommendation","No recommendation","Yes for buildings > 10,000 sq ft  (930 sq m) only","Yes ","Yes ","Yes ","Yes ","Yes "]
[null,"Continuous Air Barriers","Continuous air barrier","Entire building envelope","Entire building envelope","Entire building envelope","Entire building envelope","Entire building envelope","Entire building envelope","Entire building envelope","Entire building envelope"]
[null,"Vertical fenestration","WWR","20% to 40%","20% to 40%","20% to 40%","20% to 40%","20% to 40%","20% to 40%","20% to 40%","20% to 40%"]
[null,null,"Window orientation","Area of W and E windows each less than area of S windows (N in southern hemisphere)","Area of W and E windows each less than area of S windows (N in southern hemisphere)","Area of W and E windows each less than area of S windows (N in southern hemisphere)","Area of W and E windows each less than area of S windows (N in southern hemisphere)","Area of W and E windows each less than area of S windows (N in southern hemisphere)","Area of W and E windows each less than area of S windows (N in southern hemisphere)","Area of W and E windows each less than area of S windows (N in southern hemisphere)","Area of W and E windows each less than area of S windows (N in southern hemisphere)"]
[null,null,"Exterior sun control (S, E, and W only)","PF-0.5","PF-0.5","PF-0.5","PF-0.5","PF-0.5","No recommendation","No recommendation","No recommendation"]
[null,null,"Thermal transmittance","Nonmetal framing windows = U-0.56 (U-3.18); Metal framing windows = U-0.65 (U-3.69)","Nonmetal framing windows = U-0.45 (U-2.55); Metal framing windows = U-0.65 (U-3.69)","Nonmetal framing windows = U-0.41 (U-2.33); Metal framing windows = U-0.60 (U-3.40)","Nonmetal framing windows = U-0.38 (U-2.16); Metal framing windows = U-0.39 (U-2.21)","Nonmetal framing windows = U-0.35 (U-1.99); Metal framing windows = U-0.39 (U-2.21)","Nonmetal framing windows = U-0.35 (U-1.99); Metal framing windows = U-0.39 (U-2.21)","Nonmetal framing windows = U-0.33 (U-1.87); Metal framing windows = U-0.34 (U-1.93)","Nonmetal framing windows = U-0.25 (U-1.42); Metal framing windows = U-0.34 (U-1.93)"]
[null,null,"SHGC","Nonmetal framing windows = 0.25; Metal framing windows = 0.25 ","Nonmetal framing windows = 0.25; Metal framing windows = 0.25","Nonmetal framing windows = 0.25; Metal framing windows = 0.25","Nonmetal framing windows = 0.26; Metal framing windows = 0.38","Nonmetal framing windows = 0.26; Metal framing windows = 0.38 ","Nonmetal framing windows = 0.35; Metal framing windows = 0.38","Nonmetal framing windows = 0.40; Metal framing windows = 0.40","Nonmetal framing windows = 0.40; Metal framing windows = 0.40"]
[]
[null,"Daylighting and Lighting"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Daylighting","Light-to-solar-gain ratio","Minimum VT/SHGC = 1.10","Minimum VT/SHGC = 1.10","Minimum VT/SHGC = 1.10","Minimum VT/SHGC = 1.10","Minimum VT/SHGC = 1.10","Minimum VT/SHGC = 1.10","Minimum VT/SHGC = 1.10","Minimum VT/SHGC = 1.10"]
[null,null,"Vertical fenestration EA",0.08,0.08,0.08,0.12,0.12,0.12,0.12,0.12]
[null,"Interior Finishes","Interior surface average reflectance","Ceilings = 80%; Wall surfaces = 70%; Open office partitions = 50%","Ceilings = 80%; Wall surfaces = 70%; Open office partitions = 50%","Ceilings = 80%; Wall surfaces = 70%; Open office partitions = 50%","Ceilings = 80%; Wall surfaces = 70%; Open office partitions = 50%","Ceilings = 80%; Wall surfaces = 70%; Open office partitions = 50%","Ceilings = 80%; Wall surfaces = 70%; Open office partitions = 50%","Ceilings = 80%; Wall surfaces = 70%; Open office partitions = 50%","Ceilings = 80%; Wall surfaces = 70%; Open office partitions = 50%"]
[null,null,"Open office partitions parallel to window walls","Total partition height = 36 in. (914 mm) maximum - or - Partition above desk height = min 50% translucent","Total partition height = 36 in. (914 mm) maximum - or - Partition above desk height = min 50% translucent","Total partition height = 36 in. (914 mm) maximum - or - Partition above desk height = min 50% translucent","Total partition height = 36 in. (914 mm) maximum - or - Partition above desk height = min 50% translucent","Total partition height = 36 in. (914 mm) maximum - or - Partition above desk height = min 50% translucent","Total partition height = 36 in. (914 mm) maximum - or - Partition above desk height = min 50% translucent","Total partition height = 36 in. (914 mm) maximum - or - Partition above desk height = min 50% translucent","Total partition height = 36 in. (914 mm) maximum - or - Partition above desk height = min 50% translucent"]
[null,"Interior Lighting","LPD","0.75 W/sq ft (8.07 W/sq m)","0.75 W/sq ft (8.07 W/sq m)","0.75 W/sq ft (8.07 W/sq m)","0.75 W/sq ft (8.07 W/sq m)","0.75 W/sq ft (8.07 W/sq m)","0.75 W/sq ft (8.07 W/sq m)","0.75 W/sq ft (8.07 W/sq m)","0.75 W/sq ft (8.07 W/sq m)"]
[null,null,"24-hour lighting LPD","0.075 W/sq ft (0.81 W/sq m)","0.075 W/sq ft (0.81 W/sq m)","0.075 W/sq ft (0.81 W/sq m)","0.075 W/sq ft (0.81 W/sq m)","0.075 W/sq ft (0.81 W/sq m)","0.075 W/sq ft (0.81 W/sq m)","0.075 W/sq ft (0.81 W/sq m)","0.075 W/sq ft (0.81 W/sq m)"]
[null,null,"Light source lamp efficacy (mean LPW)","T8 and T5 lamps > 2 ft (610 mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610 mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610 mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610 mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610 mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610 mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610 mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610 mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50"]
[null,null,"Ballast","4 ft (1219 mm) T8 lamp nondimming applications = NEMA Premium instant start; 4 ft (1219 mm) T8 lamp dimming applications = NEMA Premium program start; Fluorescent and HID sources = electronic","4 ft (1219 mm) T8 lamp nondimming applications = NEMA Premium instant start; 4 ft (1219 mm) T8 lamp dimming applications = NEMA Premium program start; Fluorescent and HID sources = electronic","4 ft (1219 mm) T8 lamp nondimming applications = NEMA Premium instant start; 4 ft (1219 mm) T8 lamp dimming applications = NEMA Premium program start; Fluorescent and HID sources = electronic","4 ft (1219 mm) T8 lamp nondimming applications = NEMA Premium instant start; 4 ft (1219 mm) T8 lamp dimming applications = NEMA Premium program start; Fluorescent and HID sources = electronic","4 ft (1219 mm) T8 lamp nondimming applications = NEMA Premium instant start; 4 ft (1219 mm) T8 lamp dimming applications = NEMA Premium program start; Fluorescent and HID sources = electronic","4 ft (1219 mm) T8 lamp nondimming applications = NEMA Premium instant start; 4 ft (1219 mm) T8 lamp dimming applications = NEMA Premium program start; Fluorescent and HID sources = electronic","4 ft (1219 mm) T8 lamp nondimming applications = NEMA Premium instant start; 4 ft (1219 mm) T8 lamp dimming applications = NEMA Premium program start; Fluorescent and HID sources = electronic","4 ft (1219 mm) T8 lamp nondimming applications = NEMA Premium instant start; 4 ft (1219 mm) T8 lamp dimming applications = NEMA Premium program start; Fluorescent and HID sources = electronic"]
[null,null,"Controls for daylight harvesting in open offices— locate on N and S sides of building","Dim all general fluorescent lights within primary and secondary daylight zones of open offices","Dim all general fluorescent lights within primary and secondary daylight zones of open offices","Dim all general fluorescent lights within primary and secondary daylight zones of open offices","Dim all general fluorescent lights within primary and secondary daylight zones of open offices","Dim all general fluorescent lights within primary and secondary daylight zones of open offices","Dim all general fluorescent lights within primary and secondary daylight zones of open offices","Dim all general fluorescent lights within primary and secondary daylight zones of open offices","Dim all general fluorescent lights within primary and secondary daylight zones of open offices"]
[null,null,"Automatic controls","Auto ON to 50% = private offices, conference and meeting rooms, lounge and break rooms, copy rooms, storage rooms; Auto ON occupancy sensors = restrooms, electrical/mechanical rooms, open and private office task lighting; Time switch control = all other spaces","Auto ON to 50% = private offices, conference and meeting rooms, lounge and break rooms, copy rooms, storage rooms; Auto ON occupancy sensors = restrooms, electrical/mechanical rooms, open and private office task lighting; Time switch control = all other spaces","Auto ON to 50% = private offices, conference and meeting rooms, lounge and break rooms, copy rooms, storage rooms; Auto ON occupancy sensors = restrooms, electrical/mechanical rooms, open and private office task lighting; Time switch control = all other spaces","Auto ON to 50% = private offices, conference and meeting rooms, lounge and break rooms, copy rooms, storage rooms; Auto ON occupancy sensors = restrooms, electrical/mechanical rooms, open and private office task lighting; Time switch control = all other spaces","Auto ON to 50% = private offices, conference and meeting rooms, lounge and break rooms, copy rooms, storage rooms; Auto ON occupancy sensors = restrooms, electrical/mechanical rooms, open and private office task lighting; Time switch control = all other spaces","Auto ON to 50% = private offices, conference and meeting rooms, lounge and break rooms, copy rooms, storage rooms; Auto ON occupancy sensors = restrooms, electrical/mechanical rooms, open and private office task lighting; Time switch control = all other spaces","Auto ON to 50% = private offices, conference and meeting rooms, lounge and break rooms, copy rooms, storage rooms; Auto ON occupancy sensors = restrooms, electrical/mechanical rooms, open and private office task lighting; Time switch control = all other spaces","Auto ON to 50% = private offices, conference and meeting rooms, lounge and break rooms, copy rooms, storage rooms; Auto ON occupancy sensors = restrooms, electrical/mechanical rooms, open and private office task lighting; Time switch control = all other spaces"]
[null,"Exterior Lighting","Façade and Landscape lighting","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am"]
[null,null,"Parking lots and drives","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)"]
[null,null,"Walkways, plazas, and special feature areas","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)"]
[null,null,"All other exterior lighting","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)"]
[]
[null,"Plug Loads"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Equipment Choices","Laptop computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers","Minimum 2/3 of total computers"]
[null,null,"ENERGY STAR equipment","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances"]
[null,null,"Equipment power density","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances","For all computers, equipment, and appliances"]
[null,"Controls","Computer power control","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours","Network control with power saving modes and control OFF during unoccupied hours"]
[null,null,"Occupancy sensors","Desk plug strip occupancy sensors","Desk plug strip occupancy sensors","Desk plug strip occupancy sensors","Desk plug strip occupancy sensors","Desk plug strip occupancy sensors","Desk plug strip occupancy sensors","Desk plug strip occupancy sensors","Desk plug strip occupancy sensors"]
[null,null,"Timer switches","Water coolers and coffee makers control OFF during unoccupied hours","Water coolers and coffee makers control OFF during unoccupied hours","Water coolers and coffee makers control OFF during unoccupied hours","Water coolers and coffee makers control OFF during unoccupied hours","Water coolers and coffee makers control OFF during unoccupied hours","Water coolers and coffee makers control OFF during unoccupied hours","Water coolers and coffee makers control OFF during unoccupied hours","Water coolers and coffee makers control OFF during unoccupied hours"]
[null,null,"Vending machine control","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
[]
[null,"Service Water Heating"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"SWH","Gas water heater efficiency","Condensing water heaters = 90% efficiency","Condensing water heaters = 90% efficiency","Condensing water heaters = 90% efficiency","Condensing water heaters = 90% efficiency","Condensing water heaters = 90% efficiency","Condensing water heaters = 90% efficiency","Condensing water heaters = 90% efficiency","Condensing water heaters = 90% efficiency"]
[null,null,"Electric storage EF (≤12 kW, ≥20 gal (75.7 L))","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)"]
[null,null,"Point-of-use heater selection","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et"]
[null,null,"Electric heat pump water heater efficiency","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)"]
[null,null,"Pipe insulation (d < 1½ in. / d ≥ 1½ in.)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)"]
[]
[null,"HVAC"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Packaged Single-Zone \nAir-Source Heat Pumps","Cooling and heating efficiency","See Table 5-8 for efficiency","See Table 5-8 for efficiency","See Table 5-8 for efficiency","See Table 5-8 for efficiency","See Table 5-8 for efficiency","See Table 5-8 for efficiency","See Table 5-8 for efficiency","See Table 5-8 for efficiency"]
[null,null,"ESP","0.7 in. w.c. (174 Pa)","0.7 in. w.c. (174 Pa)","0.7 in. w.c. (174 Pa)","0.7 in. w.c. (174 Pa)","0.7 in. w.c. (174 Pa)","0.7 in. w.c. (174 Pa)","0.7 in. w.c. (174 Pa)","0.7 in. w.c. (174 Pa)"]
[null,null,"DOAS air-source heat pump","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
[null,null,"DOAS heating and cooling efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency"]
[null,null,"DOAS energy recovery","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness"]
[null,null,"DOAS fan—ESP","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum"]
[null,"WSHPs with DOAS","Unit size","5 tons (17.6 kW) or less ","5 tons (17.6 kW) or less ","5 tons (17.6 kW) or less ","5 tons (17.6 kW) or less ","5 tons (17.6 kW) or less ","5 tons (17.6 kW) or less ","5 tons (17.6 kW) or less ","5 tons (17.6 kW) or less "]
[null,null,"Single-stage cooling and heating efficiency","Cooling = 16.4 EER (Cooling = 4.81 COP); Heating = 5.2 COP ","Cooling = 16.4 EER (Cooling = 4.81 COP); Heating = 5.2 COP ","Cooling = 16.4 EER (Cooling = 4.81 COP); Heating = 5.2 COP ","Cooling = 16.4 EER (Cooling = 4.81 COP); Heating = 5.2 COP ","Cooling = 16.4 EER (Cooling = 4.81 COP); Heating = 5.2 COP ","Cooling = 16.4 EER (Cooling = 4.81 COP); Heating = 5.2 COP ","Cooling = 16.4 EER (Cooling = 4.81 COP); Heating = 5.2 COP ","Cooling = 16.4 EER (Cooling = 4.81 COP); Heating = 5.2 COP "]
[null,null,"Two-stage cooling and heating efficiency","Cooling part load = 17.6 EER; Cooling full load = 15.0 EER (Cooling part load = 5.16 COP; Cooling full load = 4.4 COP); Heating part load = 5.7 COP; Heating full load = 5.0 COP","Cooling part load = 17.6 EER; Cooling full load = 15.0 EER (Cooling part load = 5.16 COP; Cooling full load = 4.4 COP); Heating part load = 5.7 COP; Heating full load = 5.0 COP","Cooling part load = 17.6 EER; Cooling full load = 15.0 EER (Cooling part load = 5.16 COP; Cooling full load = 4.4 COP); Heating part load = 5.7 COP; Heating full load = 5.0 COP","Cooling part load = 17.6 EER; Cooling full load = 15.0 EER (Cooling part load = 5.16 COP; Cooling full load = 4.4 COP); Heating part load = 5.7 COP; Heating full load = 5.0 COP","Cooling part load = 17.6 EER; Cooling full load = 15.0 EER (Cooling part load = 5.16 COP; Cooling full load = 4.4 COP); Heating part load = 5.7 COP; Heating full load = 5.0 COP","Cooling part load = 17.6 EER; Cooling full load = 15.0 EER (Cooling part load = 5.16 COP; Cooling full load = 4.4 COP); Heating part load = 5.7 COP; Heating full load = 5.0 COP","Cooling part load = 17.6 EER; Cooling full load = 15.0 EER (Cooling part load = 5.16 COP; Cooling full load = 4.4 COP); Heating part load = 5.7 COP; Heating full load = 5.0 COP","Cooling part load = 17.6 EER; Cooling full load = 15.0 EER (Cooling part load = 5.16 COP; Cooling full load = 4.4 COP); Heating part load = 5.7 COP; Heating full load = 5.0 COP"]
[null,null,"WSHP fan—ESP","0.5 in. w.c. (124.5 Pa)","0.5 in. w.c. (124.5 Pa)","0.5 in. w.c. (124.5 Pa)","0.5 in. w.c. (124.5 Pa)","0.5 in. w.c. (124.5 Pa)","0.5 in. w.c. (124.5 Pa)","0.5 in. w.c. (124.5 Pa)","0.5 in. w.c. (124.5 Pa)"]
[null,null,"Condensing boiler efficiency",0.9,0.9,0.9,0.9,0.9,0.9,0.9,0.9]
[null,null,"DOAS water-to-water heat pump","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency"]
[null,null,"DOAS variable airflow with DCV","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
[null,null,"DOAS energy recovery","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness"]
[null,null,"DOAS fan and motor","65% mechanical efficiency; Motor efficiency per Standard 90.1-2010, Table 10.8B; VSD efficiency = 95%","65% mechanical efficiency; Motor efficiency per Standard 90.1-2010, Table 10.8B; VSD efficiency = 95%","65% mechanical efficiency; Motor efficiency per Standard 90.1-2010, Table 10.8B; VSD efficiency = 95%","65% mechanical efficiency; Motor efficiency per Standard 90.1-2010, Table 10.8B; VSD efficiency = 95%","65% mechanical efficiency; Motor efficiency per Standard 90.1-2010, Table 10.8B; VSD efficiency = 95%","65% mechanical efficiency; Motor efficiency per Standard 90.1-2010, Table 10.8B; VSD efficiency = 95%","65% mechanical efficiency; Motor efficiency per Standard 90.1-2010, Table 10.8B; VSD efficiency = 95%","65% mechanical efficiency; Motor efficiency per Standard 90.1-2010, Table 10.8B; VSD efficiency = 95%"]
[null,"VAV DX with Indirect \nGas-Fired or Electric Internal Heat and Electric Perimeter Heat","DX efficiency","See Table 5-9 for efficiency","See Table 5-9 for efficiency","See Table 5-9 for efficiency","See Table 5-9 for efficiency","See Table 5-9 for efficiency","See Table 5-9 for efficiency","See Table 5-9 for efficiency","See Table 5-9 for efficiency"]
[null,null,"Low-temperature air supply and SAT reset","50°F to 58°F (10°C to 14.4°C)","50°F to 58°F (10°C to 14.4°C)","50°F to 58°F (10°C to 14.4°C)","50°F to 58°F (10°C to 14.4°C)","50°F to 61°F (10°C to 16.1°C)","50°F to 61°F (10°C to 16.1°C)","50°F to 61°F (10°C to 16.1°C)","50°F to 61°F (10°C to 16.1°C)"]
[null,null,"Perimeter convector heat source","Electric","Electric","Electric","Electric","Hot water","Hot water","Hot water","Hot water"]
[null,null,"Gas furnace in DX units","No recommendation","No recommendation","No recommendation","No recommendation",0.9,0.9,0.9,0.9]
[null,null,"Economizer","No recommendation","≥54,000 Btu/h (15.81 kW), differential enthalpy control (Climate zone 2A); ≥54,000 Btu/h (15.81 kW), differential dry-bulb control (Climate zone 2B)","≥54,000 Btu/h (15.81 kW), differential enthalpy control (Climate zone 3A); ≥54,000 Btu/h (15.81 kW), differential dry-bulb control (Climate zones 3B and 3C)","≥54,000 Btu/h (15.81 kW), differential enthalpy control (Climate zone 4A); ≥54,000 Btu/h (15.81 kW), differential dry-bulb control (Climate zones 4B and 4C)","≥54,000 Btu/h (15.81 kW), differential dry-bulb control ","≥54,000 Btu/h (15.81 kW), differential dry-bulb control ","≥54,000 Btu/h (15.81 kW), differential dry-bulb control ","≥54,000 Btu/h (15.81 kW), differential dry-bulb control "]
[null,null,"Energy recovery","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness"]
[null,null,"Indirect evaporative cooling","No recommendation","Climate zone 2B only","Climate zone 3B only","Climate zone 4B only","Climate zone 5B only","No recommendation","No recommendation","No recommendation"]
[null,null,"Demand control and ventilation reset","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
[null,null,"ESP","2.0 in. w.c. (498 Pa)","2.0 in. w.c. (498 Pa)","2.0 in. w.c. (498 Pa)","2.0 in. w.c. (498 Pa)","2.0 in. w.c. (498 Pa)","2.0 in. w.c. (498 Pa)","2.0 in. w.c. (498 Pa)","2.0 in. w.c. (498 Pa)"]
[null,"VAV CHW \n(same as VAV DX except...)","Air-cooled chiller efficiency","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)"]
[null,null,"Air-cooled chiller IPLV","12.5 IPLV < 150 tons, 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons, 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons, 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons, 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons, 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons, 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons, 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons, 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)"]
[null,null,"Variable-speed pumping","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
[null,null,"Maximum fan power","0.72 W/cfm (0.34 W/L/s)","0.72 W/cfm (0.34 W/L/s)","0.72 W/cfm (0.34 W/L/s)","0.72 W/cfm (0.34 W/L/s)","0.72 W/cfm (0.34 W/L/s)","0.72 W/cfm (0.34 W/L/s)","0.72 W/cfm (0.34 W/L/s)","0.72 W/cfm (0.34 W/L/s)"]
[null,"Fan-Coils with DOAS","Air-cooled chiller efficiency","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)"]
[null,null,"Air-cooled chiller IPLV","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)"]
[null,null,"Condensing boiler efficiency",0.9,0.9,0.9,0.9,0.9,0.9,0.9,0.9]
[null,null,"Variable-speed pumping","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
[null,null,"VAV fan-coil units","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
[null,null,"Fan-coil unit fan power","0.30 W/cfm (0.14 W/L/s)","0.30 W/cfm (0.14 W/L/s)","0.30 W/cfm (0.14 W/L/s)","0.30 W/cfm (0.14 W/L/s)","0.30 W/cfm (0.14 W/L/s)","0.30 W/cfm (0.14 W/L/s)","0.30 W/cfm (0.14 W/L/s)","0.30 W/cfm (0.14 W/L/s)"]
[null,null,"DOAS chilled-water and hot-water coils served by same plant as fan-coils","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
[null,null,"DOAS variable airflow with DCV","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
[null,null,"DOAS energy recovery","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness"]
[null,null,"DOAS fan and motor","65% mechanical efficiency, motor efficiency; Standard 90.1-2010, Table 10.8B","65% mechanical efficiency, motor efficiency; Standard 90.1-2010, Table 10.8B","65% mechanical efficiency, motor efficiency; Standard 90.1-2010, Table 10.8B","65% mechanical efficiency, motor efficiency; Standard 90.1-2010, Table 10.8B","65% mechanical efficiency, motor efficiency; Standard 90.1-2010, Table 10.8B","65% mechanical efficiency, motor efficiency; Standard 90.1-2010, Table 10.8B","65% mechanical efficiency, motor efficiency; Standard 90.1-2010, Table 10.8B","65% mechanical efficiency, motor efficiency; Standard 90.1-2010, Table 10.8B"]
[null,"Radiant Systems with DOAS","Air-cooled chiller full-load efficiency","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)","10 EER (2.93 COP)"]
[null,null,"Air-cooled chiller IPLV","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)","12.5 IPLV < 150 tons; 12.75 IPLV ≥ 150 tons (3.66 IPLV < 528 kW, 3.74 IPLV ≥ 528 kW)"]
[null,null,"Condensing boiler efficiency",0.9,0.9,0.9,0.9,0.9,0.9,0.9,0.9]
[null,null,"DOAS heating and cooling efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency","See Table 5-10 for efficiency"]
[null,null,"DOAS variable airflow with DCV","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
[null,null,"DOAS energy recovery","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness","Yes, see Table 5-11 for effectiveness"]
[null,null,"DOAS fan—ESP","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum","1.5 in. w.c. (374 Pa) maximum"]
[null,"Ducts and Dampers","OA damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper"]
[null,null,"Friction rate","0.08 in. w.c./100 feet (19.92 Pa/30.5 m)","0.08 in. w.c./100 feet (19.92 Pa/30.5 m)","0.08 in. w.c./100 feet (19.92 Pa/30.5 m)","0.08 in. w.c./100 feet (19.92 Pa/30.5 m)","0.08 in. w.c./100 feet (19.92 Pa/30.5 m)","0.08 in. w.c./100 feet (19.92 Pa/30.5 m)","0.08 in. w.c./100 feet (19.92 Pa/30.5 m)","0.08 in. w.c./100 feet (19.92 Pa/30.5 m)"]
[null,null,"Sealing","Seal class B","Seal class B","Seal class B","Seal class B","Seal class B","Seal class B","Seal class B","Seal class B"]
[null,null,"Location","Interior only","Interior only","Interior only","Interior only","Interior only","Interior only","Interior only","Interior only"]
[null,null,"Insulation level","R-6.0 (R-1.1)","R-6.0 (R-1.1)","R-6.0 (R-1.1)","R-6.0 (R-1.1)","R-6.0 (R-1.1)","R-6.0 (R-1.1)","R-6.0 (R-1.1)","R-6.0 (R-1.1)"]

{"sheet":"Medium to Big Box Retail","index":4,"n_rows":105,"n_cols":12,"rows_kept":105,"cut":false,"hidden":false,"merged":[[88,1,91,1],[92,1,95,1],[96,1,98,1],[100,1,100,12],[102,1,104,1],[81,1,87,1],[27,1,42,1],[27,2,29,2],[30,2,33,2],[38,2,42,2],[43,1,46,1],[50,1,54,1],[55,1,59,1],[63,1,67,1],[71,1,73,1],[74,1,76,1],[77,1,80,1],[21,1,23,1],[6,1,8,1],[9,1,11,1],[12,1,13,1],[14,1,15,1],[16,1,19,1]]}
[]
[null,"ASHRAE 50% Advanced Energy Design Guide for Medium to Big Box Retail Buildings"]
[]
[]
[null,"Envelope"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Roof","Insulation entirely above deck","R-20.0 (R-3.5) c.i.","R-25.0 (R-4.4) c.i.","R-25.0 (R-4.4) c.i.","R-25.0 (R-4.4) c.i.","R-30.0 (R-5.53) c.i.","R-30.0 (R-5.53) c.i.","R-35.0 (R-6.2) c.i.","R-35.0 (R-6.2) c.i."]
[null,null,"Metal building","R-19.0 + R-10.0 FC (R-3.3 + R-1.8 FC) ","R-19.0 + R-10.0 FC (R-3.3 + R-1.8 FC) ","R-19.0 + R-10.0 FC (R-3.3 + R-1.8 FC) ","R-19.0 + R-11.0 Ls (R-3.3 + R-1.9 Ls)","R-19.0 + R-11.0 Ls (R-3.3 + R-1.9 Ls)","R-25.0 + R-11.0 Ls (R-4.4 + R-1.9 Ls)","R-30.0 + R-11.0 Ls (R-5.3 + R-1.9 Ls)","R-30.0 + R-11.0 Ls (R-5.3 + R-1.9 Ls)"]
[null,null,"SRI",78,78,78,"No recommendation","No recommendation","No recommendation","No recommendation","No recommendation"]
[null,"Walls","Mass (HC > 7 Btu/sq ft·°F (143 kJ/sq m·K))","No recommendation","R-5.7 (R-1.0) c.i.","R-7.6 (R-1.3) c.i.","R-9.5 (R-1.7) c.i.","R-11.4 (R-2.0) c.i.","R-15.4 (R-2.7) c.i.","R-17.0 (R-3.0) c.i.","R-19.0 (R-3.3) c.i."]
[null,null,"Metal building","R-0.0 + R-9.8 c.i. (R-0.0 + R-1.7 c.i.) ","R-0.0 + R-9.8 c.i. (R-0.0 + R-1.7 c.i.)","R-0.0 + R-13.0 c.i. (R-0.0 + R-2.3 c.i.)","R-0.0 + R-15.8 c.i. (R-0.0 + R-2.8 c.i.)","R-0.0 + R-19 c.i. (R-0.0 + R-3.3 c.i.)","R-0.0 + R-19 c.i. (R-0.0 + R-3.3 c.i.)","R-0.0 + R-22.1 c.i. (R-0.0 + R-3.9 c.i.)","R-0.0 + R-25 c.i. (R-0.0 + R-4.4 c.i.)"]
[null,null,"Steel-framed","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-7.5 c.i. (R-2.3 + R-1.3 c.i.)","R-13.0 + R-10.0 c.i. (R-2.3 + R-1.8 c.i.)","R-13.0 + R-12.5 c.i. (R-2.3 + R-2.2 c.i.)","R-13.0 + R-15.0 c.i. (R-2.3 + R-2.6 c.i.)","R-13.0 + R-18.8 c.i. (R-2.3 + R-3.3 c.i.)","R-13.0 + R-18.8 c.i. (R-2.3 + R-3.3 c.i.)"]
[null,"Floors","Mass","No recommendation","R-10.4 (R-1.8) c.i.","R-12.5 (R-2.2) c.i.","R-14.6 (R-2.6) c.i.","R-14.6 (R-2.6) c.i.","R-16.7 (R-2.9) c.i.","R-20.9 (R-3.7) c.i.","R-23.0 (R-4.1) c.i."]
[null,null,"Steel-framed","No recommendation","R-30.0 (R-5.3)","R-30.0 (R-5.3)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-38.0 (R-6.7)","R-49.0 (R-8.6)","R-60.0 (R-10.6)"]
[null,"Slabs","Unheated","No recommendation","No recommendation","No recommendation","R-15 for 24 in. (R-2.6 for 610 mm)","R-15 for 24 in. (R-2.6 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)"]
[null,null,"Heated","R-7.5 (R-1.32) for 12 in. (305 mm)","R-10 for 24 in. (R-1.8 for 610 mm)","R-10 for 24 in. (R-1.8 for 610 mm)","R-20 for 24 in. (R-3.5 for 610 mm)","R-20 for 48 in.  (R-3.5 for 1220 mm)","R-20 for 48 in.  (R-3.5 for 1220 mm)","R-25 for 48 in.  (R-4.4 for 1220 mm)","R-25 for 48 in.  (R-4.4 for 1220 mm)"]
[null,"Doors","Swinging","U-0.70 (U-3.97)","U-0.70 (U-3.97)","U-0.70 (U-3.97)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)","U-0.50 (U-2.84)"]
[null,null,"Non-swinging","Roll-up = U-0.25 (U-1.42); All other = U-0.07 (U-0.40)","Roll-up = U-0.25 (U-1.42); All other = U-0.07 (U-0.40)","Roll-up = U-0.25 (U-1.42); All other = U-0.07 (U-0.40)","Roll-up = U-0.25 (U-1.42); All other = U-0.07 (U-0.40)","Roll-up = U-0.25 (U-1.42); All other = U-0.07 (U-0.40)","Roll-up = U-0.25 (U-1.42); All other = U-0.07 (U-0.40)","Roll-up = U-0.25 (U-1.42); All other = U-0.07 (U-0.40)","Roll-up = U-0.25 (U-1.42); All other = U-0.07 (U-0.40)"]
[null,null,"Vehicular/dock infiltration—door closed","0.28 cfm/sq ft of door area (1.42 L/s/sq m)","0.28 cfm/sq ft of door area (1.42 L/s/sq m)","0.28 cfm/sq ft of door area (1.42 L/s/sq m)","0.28 cfm/sq ft of door area (1.42 L/s/sq m)","0.28 cfm/sq ft of door area (1.42 L/s/sq m)","0.28 cfm/sq ft of door area (1.42 L/s/sq m)","0.28 cfm/sq ft of door area (1.42 L/s/sq m)","0.28 cfm/sq ft of door area (1.42 L/s/sq m)"]
[null,null,"Vehicular/dock infiltration—door open, truck in place","Weather seals for dock, levelers, trailer hinges","Weather seals for dock, levelers, trailer hinges","Weather seals for dock, levelers, trailer hinges","Weather seals for dock, levelers, trailer hinges","Weather seals for dock, levelers, trailer hinges","Weather seals for dock, levelers, trailer hinges","Weather seals for dock, levelers, trailer hinges","Weather seals for dock, levelers, trailer hinges"]
[null,"Vestibules","At building entrance","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
[null,"View fenestration \n(all orientations)","Thermal transmittance","U-1.20 (U-6.81)","U-0.70 (U-3.97)","U-0.60 (U-3.40)","U-0.50 (U-2.84)","U-0.45 (U-2.55)","U-0.45 (U-2.55)","U-0.40 (U-2.27)","U-0.40 (U-2.27)"]
[null,null,"SHGC",0.25,0.25,0.25,0.4,0.4,0.4,0.45,0.45]
[null,null,"VT",0.25,0.25,0.32,0.51,0.51,0.51,0.45,0.45]
[]
[null,"Daylighting and Lighting"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Interior Lighting","LPD - Ambient Lighting","Sales floor = 1.15 W/sq ft (12.38 W/sq m)","Sales floor = 1.15 W/sq ft (12.38 W/sq m)","Sales floor = 1.15 W/sq ft (12.38 W/sq m)","Sales floor = 1.15 W/sq ft (12.38 W/sq m)","Sales floor = 1.15 W/sq ft (12.38 W/sq m)","Sales floor = 1.15 W/sq ft (12.38 W/sq m)","Sales floor = 1.15 W/sq ft (12.38 W/sq m)","Sales floor = 1.15 W/sq ft (12.38 W/sq m)"]
[null,null,null,"Stock room = 0.6 W/sq ft (6.46 W/sq m)","Stock room = 0.6 W/sq ft (6.46 W/sq m)","Stock room = 0.6 W/sq ft (6.46 W/sq m)","Stock room = 0.6 W/sq ft (6.46 W/sq m)","Stock room = 0.6 W/sq ft (6.46 W/sq m)","Stock room = 0.6 W/sq ft (6.46 W/sq m)","Stock room = 0.6 W/sq ft (6.46 W/sq m)","Stock room = 0.6 W/sq ft (6.46 W/sq m)"]
[null,null,null,"Average of all other = 0.9 W/sq ft (9.69 W/sq m)","Average of all other = 0.9 W/sq ft (9.69 W/sq m)","Average of all other = 0.9 W/sq ft (9.69 W/sq m)","Average of all other = 0.9 W/sq ft (9.69 W/sq m)","Average of all other = 0.9 W/sq ft (9.69 W/sq m)","Average of all other = 0.9 W/sq ft (9.69 W/sq m)","Average of all other = 0.9 W/sq ft (9.69 W/sq m)","Average of all other = 0.9 W/sq ft (9.69 W/sq m)"]
[null,null,"LPD - Additional specialty sales floor lighting","Sporting goods, small electronics = 0.6 W/sq ft (6.46 W/sq m)","Sporting goods, small electronics = 0.6 W/sq ft (6.46 W/sq m)","Sporting goods, small electronics = 0.6 W/sq ft (6.46 W/sq m)","Sporting goods, small electronics = 0.6 W/sq ft (6.46 W/sq m)","Sporting goods, small electronics = 0.6 W/sq ft (6.46 W/sq m)","Sporting goods, small electronics = 0.6 W/sq ft (6.46 W/sq m)","Sporting goods, small electronics = 0.6 W/sq ft (6.46 W/sq m)","Sporting goods, small electronics = 0.6 W/sq ft (6.46 W/sq m)"]
[null,null,null,"Furniture, clothing, cosmetics, art = 0.95 W/sq ft (10.23 W/sq m)","Furniture, clothing, cosmetics, art = 0.95 W/sq ft (10.23 W/sq m)","Furniture, clothing, cosmetics, art = 0.95 W/sq ft (10.23 W/sq m)","Furniture, clothing, cosmetics, art = 0.95 W/sq ft (10.23 W/sq m)","Furniture, clothing, cosmetics, art = 0.95 W/sq ft (10.23 W/sq m)","Furniture, clothing, cosmetics, art = 0.95 W/sq ft (10.23 W/sq m)","Furniture, clothing, cosmetics, art = 0.95 W/sq ft (10.23 W/sq m)","Furniture, clothing, cosmetics, art = 0.95 W/sq ft (10.23 W/sq m)"]
[null,null,null,"Jewelry, crystal, china = 1.5 W/sq ft (16.15 W/sq m)","Jewelry, crystal, china = 1.5 W/sq ft (16.15 W/sq m)","Jewelry, crystal, china = 1.5 W/sq ft (16.15 W/sq m)","Jewelry, crystal, china = 1.5 W/sq ft (16.15 W/sq m)","Jewelry, crystal, china = 1.5 W/sq ft (16.15 W/sq m)","Jewelry, crystal, china = 1.5 W/sq ft (16.15 W/sq m)","Jewelry, crystal, china = 1.5 W/sq ft (16.15 W/sq m)","Jewelry, crystal, china = 1.5 W/sq ft (16.15 W/sq m)"]
[null,null,null,"All other = 0.4 W/sq ft (4.31 W/sq m)","All other = 0.4 W/sq ft (4.31 W/sq m)","All other = 0.4 W/sq ft (4.31 W/sq m)","All other = 0.4 W/sq ft (4.31 W/sq m)","All other = 0.4 W/sq ft (4.31 W/sq m)","All other = 0.4 W/sq ft (4.31 W/sq m)","All other = 0.4 W/sq ft (4.31 W/sq m)","All other = 0.4 W/sq ft (4.31 W/sq m)"]
[null,null,"Light source efficacy (mean LPW)","T8 and T5 lamps > 2 ft (610mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50","T8 and T5 lamps > 2 ft (610mm) = 92; T8 and T5 lamps ≤ 2 ft (610 mm) = 85; All other > 50"]
[null,null,"T8 ballasts","Nondimming = NEMA Premium Instant Start; Dimming = NEMA Premium Programmed Start","Nondimming = NEMA Premium Instant Start; Dimming = NEMA Premium Programmed Start","Nondimming = NEMA Premium Instant Start\nDimming = NEMA Premium Programmed Start","Nondimming = NEMA Premium Instant Start; Dimming = NEMA Premium Programmed Start","Nondimming = NEMA Premium Instant Start; Dimming = NEMA Premium Programmed Start","Nondimming = NEMA Premium Instant Start; Dimming = NEMA Premium Programmed Start","Nondimming = NEMA Premium Instant Start; Dimming = NEMA Premium Programmed Start","Nondimming = NEMA Premium Instant Start; Dimming = NEMA Premium Programmed Start"]
[null,null,"All T5/T5HO ballasts","Electronic programmed start","Electronic programmed start","Electronic programmed start","Electronic programmed start","Electronic programmed start","Electronic programmed start","Electronic programmed start","Electronic programmed start"]
[null,null,"All CFL and HID ballasts","Electronic","Electronic","Electronic","Electronic","Electronic","Electronic","Electronic","Electronic"]
[null,null,"Lighting controls","Sales floor = Time switch—auto to 25% 3 h before and after store open hours; auto to 2% or less after hours","Sales floor = Time switch—auto to 25% 3 h before and after store open hours; auto to 2% or less after hours","Sales floor = Time switch—auto to 25% 3 h before and after store open hours; auto to 2% or less after hours","Sales floor = Time switch—auto to 25% 3 h before and after store open hours; auto to 2% or less after hours","Sales floor = Time switch—auto to 25% 3 h before and after store open hours; auto to 2% or less after hours","Sales floor = Time switch—auto to 25% 3 h before and after store open hours; auto to 2% or less after hours","Sales floor = Time switch—auto to 25% 3 h before and after store open hours; auto to 2% or less after hours","Sales floor = Time switch—auto to 25% 3 h before and after store open hours; auto to 2% or less after hours"]
[null,null,null,"Additional specialty lighting = auto ON only during store open hours","Additional specialty lighting = auto ON only during store open hours","Additional specialty lighting = auto ON only during store open hours","Additional specialty lighting = auto ON only during store open hours","Additional specialty lighting = auto ON only during store open hours","Additional specialty lighting = auto ON only during store open hours","Additional specialty lighting = auto ON only during store open hours","Additional specialty lighting = auto ON only during store open hours"]
[null,null,null,"Stock room, restrooms = auto ON/OFF occupancy sensors","Stock room, restrooms = auto ON/OFF occupancy sensors","Stock room, restrooms = auto ON/OFF occupancy sensors","Stock room, restrooms = auto ON/OFF occupancy sensors","Stock room, restrooms = auto ON/OFF occupancy sensors","Stock room, restrooms = auto ON/OFF occupancy sensors","Stock room, restrooms = auto ON/OFF occupancy sensors","Stock room, restrooms = auto ON/OFF occupancy sensors"]
[null,null,null,"All other = manual ON, auto OFF occupancy sensors","All other = manual ON, auto OFF occupancy sensors","All other = manual ON, auto OFF occupancy sensors","All other = manual ON, auto OFF occupancy sensors","All other = manual ON, auto OFF occupancy sensors","All other = manual ON, auto OFF occupancy sensors","All other = manual ON, auto OFF occupancy sensors","All other = manual ON, auto OFF occupancy sensors"]
[null,null,null,"After hours = max 2% of total building LPD","After hours = max 2% of total building LPD","After hours = max 2% of total building LPD","After hours = max 2% of total building LPD","After hours = max 2% of total building LPD","After hours = max 2% of total building LPD","After hours = max 2% of total building LPD","After hours = max 2% of total building LPD"]
[null,"Exterior Lighting","Façade and landscape lighting","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am","LPD = 0.075 W/sq ft (0.81 W/sq m) in LZ3 and LZ4, 0.05 W/sq ft (0.54 W/sq m) in LZ2; Controls = auto OFF between 12 am and 6 am"]
[null,null,"Parking lots and drives","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.1 W/sq ft (1.08 W/sq m) in LZ3 and LZ4, 0.06 W/sq ft (0.65 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)"]
[null,null,"Walkways, plazas, and special feature areas","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)","LPD = 0.16 W/sq ft (1.72 W/sq m) LZ3 and LZ4, 0.14 W/sq ft (1.51 W/sq m) in LZ2; Controls = auto reduce to 25% (12 am to 6 am)"]
[null,null,"All other exterior lighting","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)","LPD = follow Standard 90.1-2010; Controls = auto reduce to 25% (12 am to 6 am)"]
[]
[null,"Plug Loads"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Equipment Choices","ENERGY STAR equipment","All illuminated signage, security monitors, computers, equipment, and appliances (where available)","All illuminated signage, security monitors, computers, equipment, and appliances (where available)","All illuminated signage, security monitors, computers, equipment, and appliances (where available)","All illuminated signage, security monitors, computers, equipment, and appliances (where available)","All illuminated signage, security monitors, computers, equipment, and appliances (where available)","All illuminated signage, security monitors, computers, equipment, and appliances (where available)","All illuminated signage, security monitors, computers, equipment, and appliances (where available)","All illuminated signage, security monitors, computers, equipment, and appliances (where available)"]
[null,null,"Vending machines","Delamp in break rooms and specify best-in-class efficiency; Specify load managing systems for refrigerated vending","Delamp in break rooms and specify best-in-class efficiency; Specify load managing systems for refrigerated vending","Delamp in break rooms and specify best-in-class efficiency; Specify load managing systems for refrigerated vending","Delamp in break rooms and specify best-in-class efficiency; Specify load managing systems for refrigerated vending","Delamp in break rooms and specify best-in-class efficiency; Specify load managing systems for refrigerated vending","Delamp in break rooms and specify best-in-class efficiency; Specify load managing systems for refrigerated vending","Delamp in break rooms and specify best-in-class efficiency; Specify load managing systems for refrigerated vending","Delamp in break rooms and specify best-in-class efficiency; Specify load managing systems for refrigerated vending"]
[null,null,"Procurement","Incorporate control and efficiency options in negotiations for all third-party owned plug loads; Consolidate equipment where possible","Incorporate control and efficiency options in negotiations for all third-party owned plug loads; Consolidate equipment where possible","Incorporate control and efficiency options in negotiations for all third-party owned plug loads; Consolidate equipment where possible","Incorporate control and efficiency options in negotiations for all third-party owned plug loads; Consolidate equipment where possible","Incorporate control and efficiency options in negotiations for all third-party owned plug loads; Consolidate equipment where possible","Incorporate control and efficiency options in negotiations for all third-party owned plug loads; Consolidate equipment where possible","Incorporate control and efficiency options in negotiations for all third-party owned plug loads; Consolidate equipment where possible","Incorporate control and efficiency options in negotiations for all third-party owned plug loads; Consolidate equipment where possible"]
[null,null,"Computers","Specify laptops, tablets, or mini-desktops where feasible","Specify laptops, tablets, or mini-desktops where feasible","Specify laptops, tablets, or mini-desktops where feasible","Specify laptops, tablets, or mini-desktops where feasible","Specify laptops, tablets, or mini-desktops where feasible","Specify laptops, tablets, or mini-desktops where feasible","Specify laptops, tablets, or mini-desktops where feasible","Specify laptops, tablets, or mini-desktops where feasible"]
[null,null,"Signage","Use LED internally illuminated where applicable; Consolidate/replace static media with dynamic","Use LED internally illuminated where applicable; Consolidate/replace static media with dynamic","Use LED internally illuminated where applicable; Consolidate/replace static media with dynamic","Use LED internally illuminated where applicable; Consolidate/replace static media with dynamic","Use LED internally illuminated where applicable; Consolidate/replace static media with dynamic","Use LED internally illuminated where applicable; Consolidate/replace static media with dynamic","Use LED internally illuminated where applicable; Consolidate/replace static media with dynamic","Use LED internally illuminated where applicable; Consolidate/replace static media with dynamic"]
[null,"Controls","Sales floor plug control","Auto control all display outlets that can be turned off during nonbusiness hours and all other sales outlets that can be turned off during unoccupied hours; Specify auto standby modes for third-party owned/supplied plug loads","Auto control all display outlets that can be turned off during nonbusiness hours and all other sales outlets that can be turned off during unoccupied hours; Specify auto standby modes for third-party owned/supplied plug loads","Auto control all display outlets that can be turned off during nonbusiness hours and all other sales outlets that can be turned off during unoccupied hours; Specify auto standby modes for third-party owned/supplied plug loads","Auto control all display outlets that can be turned off during nonbusiness hours and all other sales outlets that can be turned off during unoccupied hours; Specify auto standby modes for third-party owned/supplied plug loads","Auto control all display outlets that can be turned off during nonbusiness hours and all other sales outlets that can be turned off during unoccupied hours; Specify auto standby modes for third-party owned/supplied plug loads","Auto control all display outlets that can be turned off during nonbusiness hours and all other sales outlets that can be turned off during unoccupied hours; Specify auto standby modes for third-party owned/supplied plug loads","Auto control all display outlets that can be turned off during nonbusiness hours and all other sales outlets that can be turned off during unoccupied hours; Specify auto standby modes for third-party owned/supplied plug loads","Auto control all display outlets that can be turned off during nonbusiness hours and all other sales outlets that can be turned off during unoccupied hours; Specify auto standby modes for third-party owned/supplied plug loads"]
[null,null,"Computer power control","Network control with power-saving modes and control during unoccupied hours","Network control with power-saving modes and control during unoccupied hours","Network control with power-saving modes and control during unoccupied hours","Network control with power-saving modes and control during unoccupied hours","Network control with power-saving modes and control during unoccupied hours","Network control with power-saving modes and control during unoccupied hours","Network control with power-saving modes and control during unoccupied hours","Network control with power-saving modes and control during unoccupied hours"]
[null,null,"Occupancy sensors","Office/break/security room plug strip occupancy sensors; Other equipment as applicable","Office/break/security room plug strip occupancy sensors; Other equipment as applicable","Office/break/security room plug strip occupancy sensors; Other equipment as applicable","Office/break/security room plug strip occupancy sensors; Other equipment as applicable","Office/break/security room plug strip occupancy sensors; Other equipment as applicable","Office/break/security room plug strip occupancy sensors; Other equipment as applicable","Office/break/security room plug strip occupancy sensors; Other equipment as applicable","Office/break/security room plug strip occupancy sensors; Other equipment as applicable"]
[null,null,"Timer switches","Water coolers, coffee makers, other small appliances auto shut-off during unoccupied hours","Water coolers, coffee makers, other small appliances auto shut-off during unoccupied hours","Water coolers, coffee makers, other small appliances auto shut-off during unoccupied hours","Water coolers, coffee makers, other small appliances auto shut-off during unoccupied hours","Water coolers, coffee makers, other small appliances auto shut-off during unoccupied hours","Water coolers, coffee makers, other small appliances auto shut-off during unoccupied hours","Water coolers, coffee makers, other small appliances auto shut-off during unoccupied hours","Water coolers, coffee makers, other small appliances auto shut-off during unoccupied hours"]
[null,null,"Polices","Store policy on allowed equipment","Store policy on allowed equipment","Store policy on allowed equipment","Store policy on allowed equipment","Store policy on allowed equipment","Store policy on allowed equipment","Store policy on allowed equipment","Store policy on allowed equipment"]
[]
[null,"Service Water Heating"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"SWH","Gas water heater efficiency","Condensing water heaters = 95% efficiency","Condensing water heaters = 95% efficiency","Condensing water heaters = 95% efficiency","Condensing water heaters = 95% efficiency","Condensing water heaters = 95% efficiency","Condensing water heaters = 95% efficiency","Condensing water heaters = 95% efficiency","Condensing water heaters = 95% efficiency"]
[null,null,"Electric storage EF (≤12 kW, ≥20 gal (75.7 L))","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)","EF > 0.99 – 0.0012 × volume in gal (EF > 0.99 - 0.00032 x volume in L) (see Table 5-7)"]
[null,null,"Point-of-use heater selection","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et","0.81 EF or 81% Et"]
[null,null,"Electric heat pump water heater","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)","COP 3.0 (interior heat source)"]
[null,null,"Pipe insulation (d < 1½ in. / d ≥ 1½ in.) (d < 38 mm / d ≥ 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)","1 in. / 1 ½ in. (25.4 mm / 38 mm)"]
[]
[null,"HVAC"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"Packaged Variable-Volume DX Air Conditioners with DOAS","Heating efficiency",0.8,0.8,0.8,0.8,0.8,0.8,0.8,0.8]
[null,null,"Cooling efficiency","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)"]
[null,null,"Maximum external static pressure","Single zone = 0.7 in. w.c. (175 Pa); Multizone = 1.8 in. w.c. (450 Pa)","Single zone = 0.7 in. w.c. (175 Pa); Multizone = 1.8 in. w.c. (450 Pa)","Single zone = 0.7 in. w.c. (175 Pa); Multizone = 1.8 in. w.c. (450 Pa)","Single zone = 0.7 in. w.c. (175 Pa); Multizone = 1.8 in. w.c. (450 Pa)","Single zone = 0.7 in. w.c. (175 Pa); Multizone = 1.8 in. w.c. (450 Pa)","Single zone = 0.7 in. w.c. (175 Pa); Multizone = 1.8 in. w.c. (450 Pa)","Single zone = 0.7 in. w.c. (175 Pa); Multizone = 1.8 in. w.c. (450 Pa)","Single zone = 0.7 in. w.c. (175 Pa); Multizone = 1.8 in. w.c. (450 Pa)"]
[null,"Packaged Constant-Volume DX Air Conditioners with DOAS","Heating efficiency",0.8,0.8,0.8,0.8,0.8,0.8,0.8,0.8]
[null,null,"Cooling efficiency","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)","< 65 kBtu/h = 15.0 SEER (<19kW = 4.10 SCOP); 65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n240–760 kBtu/h = 10.5 EER, 11.3 IEER (70 kW - 220 kW = 3.10 COP, 3.31 ICOP); \n≥ 760 kBtu/h = 9.7 EER, 10.9 IEER (≥ 220 kW = 2.84 COP, 3.20 ICOP)"]
[null,null,"Maximum external static pressure","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)"]
[null,"Packaged Single-Zone Air-Source Heat Pumps with DOAS","Heating efficiency","< 65 kBtu/h = 9.0 HSPF (<19kW = 2.64 SCOP);\n 65–135 kBtu/h = 3.4 COP at 47°F; 2.4 COP at 17°F (19 kW - 40 kW = 3.4 COP at 8.3°C, 2.4 COP at -8.3°C); \n135–240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (40 kW - 70 kW =3.4 COP at 8.3°C, 2.1 COP at -8.3°C); \n≥ 240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (70 kW = 3.2 COP at 8.3°C, 2.1 COP at -8.3°C)","< 65 kBtu/h = 9.0 HSPF (<19kW = 2.64 SCOP); \n65–135 kBtu/h = 3.4 COP at 47°F; 2.4 COP at 17°F (19 kW - 40 kW = 3.4 COP at 8.3°C, 2.4 COP at -8.3°C); \n135–240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (40 kW - 70 kW =3.4 COP at 8.3°C, 2.1 COP at -8.3°C); \n≥ 240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (70 kW = 3.2 COP at 8.3°C, 2.1 COP at -8.3°C)","< 65 kBtu/h = 9.0 HSPF (<19kW = 2.64 SCOP);\n 65–135 kBtu/h = 3.4 COP at 47°F; 2.4 COP at 17°F (19 kW - 40 kW = 3.4 COP at 8.3°C, 2.4 COP at -8.3°C); \n135–240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (40 kW - 70 kW =3.4 COP at 8.3°C, 2.1 COP at -8.3°C); \n≥ 240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (70 kW = 3.2 COP at 8.3°C, 2.1 COP at -8.3°C)","< 65 kBtu/h = 9.0 HSPF (<19kW = 2.64 SCOP); \n65–135 kBtu/h = 3.4 COP at 47°F; 2.4 COP at 17°F (19 kW - 40 kW = 3.4 COP at 8.3°C, 2.4 COP at -8.3°C); \n135–240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (40 kW - 70 kW =3.4 COP at 8.3°C, 2.1 COP at -8.3°C); \n≥ 240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (70 kW = 3.2 COP at 8.3°C, 2.1 COP at -8.3°C)","< 65 kBtu/h = 9.0 HSPF (<19kW = 2.64 SCOP); \n65–135 kBtu/h = 3.4 COP at 47°F; 2.4 COP at 17°F (19 kW - 40 kW = 3.4 COP at 8.3°C, 2.4 COP at -8.3°C); \n135–240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (40 kW - 70 kW =3.4 COP at 8.3°C, 2.1 COP at -8.3°C); \n≥ 240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (70 kW = 3.2 COP at 8.3°C, 2.1 COP at -8.3°C)","< 65 kBtu/h = 9.0 HSPF (<19kW = 2.64 SCOP); \n65–135 kBtu/h = 3.4 COP at 47°F; 2.4 COP at 17°F (19 kW - 40 kW = 3.4 COP at 8.3°C, 2.4 COP at -8.3°C); \n135–240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (40 kW - 70 kW =3.4 COP at 8.3°C, 2.1 COP at -8.3°C); \n≥ 240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (70 kW = 3.2 COP at 8.3°C, 2.1 COP at -8.3°C)","< 65 kBtu/h = 9.0 HSPF (<19kW = 2.64 SCOP); \n65–135 kBtu/h = 3.4 COP at 47°F; 2.4 COP at 17°F (19 kW - 40 kW = 3.4 COP at 8.3°C, 2.4 COP at -8.3°C); \n135–240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (40 kW - 70 kW =3.4 COP at 8.3°C, 2.1 COP at -8.3°C); \n≥ 240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (70 kW = 3.2 COP at 8.3°C, 2.1 COP at -8.3°C)","< 65 kBtu/h = 9.0 HSPF (<19kW = 2.64 SCOP);\n 65–135 kBtu/h = 3.4 COP at 47°F; 2.4 COP at 17°F (19 kW - 40 kW = 3.4 COP at 8.3°C, 2.4 COP at -8.3°C); \n135–240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (40 kW - 70 kW =3.4 COP at 8.3°C, 2.1 COP at -8.3°C); \n≥ 240 kBtu/h = 3.2 COP at 47°F; 2.1 COP at 17°F (70 kW = 3.2 COP at 8.3°C, 2.1 COP at -8.3°C)"]
[null,null,"Cooling efficiency","< 65 kBtu/h = 15.0 SEER, 12.0 EER (<19kW = 4.10 SCOP, 3.52 COP); \n65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n≥ 240 kBtu/h = 10.5 EER, 11.3 IEER (≥ 70 kW = 3.10 COP, 3.31 ICOP)","< 65 kBtu/h = 15.0 SEER, 12.0 EER (<19kW = 4.10 SCOP, 3.52 COP); \n65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n≥ 240 kBtu/h = 10.5 EER, 11.3 IEER (≥ 70 kW = 3.10 COP, 3.31 ICOP)","< 65 kBtu/h = 15.0 SEER, 12.0 EER (<19kW = 4.10 SCOP, 3.52 COP); \n65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n≥ 240 kBtu/h = 10.5 EER, 11.3 IEER (≥ 70 kW = 3.10 COP, 3.31 ICOP)","< 65 kBtu/h = 15.0 SEER, 12.0 EER (<19kW = 4.10 SCOP, 3.52 COP); \n65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n≥ 240 kBtu/h = 10.5 EER, 11.3 IEER (≥ 70 kW = 3.10 COP, 3.31 ICOP)","< 65 kBtu/h = 15.0 SEER, 12.0 EER (<19kW = 4.10 SCOP, 3.52 COP); \n65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n≥ 240 kBtu/h = 10.5 EER, 11.3 IEER (≥ 70 kW = 3.10 COP, 3.31 ICOP)","< 65 kBtu/h = 15.0 SEER, 12.0 EER (<19kW = 4.10 SCOP, 3.52 COP); \n65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n≥ 240 kBtu/h = 10.5 EER, 11.3 IEER (≥ 70 kW = 3.10 COP, 3.31 ICOP)","< 65 kBtu/h = 15.0 SEER, 12.0 EER (<19kW = 4.10 SCOP, 3.52 COP); \n65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n≥ 240 kBtu/h = 10.5 EER, 11.3 IEER (≥ 70 kW = 3.10 COP, 3.31 ICOP)","< 65 kBtu/h = 15.0 SEER, 12.0 EER (<19kW = 4.10 SCOP, 3.52 COP); \n65–135 kBtu/h = 11.5 EER, 12.8 IEER (19 kW - 40 kW = 3.37 COP, 3.75 ICOP); \n135–240 kBtu/h = 11.5 EER, 12.3 IEER (40 kW - 70 kW = 3.37 COP, 3.61 ICOP); \n≥ 240 kBtu/h = 10.5 EER, 11.3 IEER (≥ 70 kW = 3.10 COP, 3.31 ICOP)"]
[null,null,"Maximum external static pressure","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)"]
[null,null,"Maximum fan power","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)"]
[null,"Packaged Single-Zone Water-Source Heat Pumps with DOAS","Heating efficiency","Full load =15.0 EER (4.40 COP); Part load= 17.6 EER (5.16 COP)","Full load =15.0 EER (4.40 COP); Part load= 17.6 EER (5.16 COP)","Full load =15.0 EER (4.40 COP); Part load= 17.6 EER (5.16 COP)","Full load =15.0 EER (4.40 COP); Part load= 17.6 EER (5.16 COP)","Full load =15.0 EER (4.40 COP); Part load= 17.6 EER (5.16 COP)","Full load =15.0 EER (4.40 COP); Part load= 17.6 EER (5.16 COP)","Full load =15.0 EER (4.40 COP); Part load= 17.6 EER (5.16 COP)","Full load =15.0 EER (4.40 COP); Part load= 17.6 EER (5.16 COP)"]
[null,null,"Cooling efficiency","Full load = 5.0 COP; Part load = 5.7 COP","Full load = 5.0 COP; Part load = 5.7 COP","Full load = 5.0 COP; Part load = 5.7 COP","Full load = 5.0 COP; Part load = 5.7 COP","Full load = 5.0 COP; Part load = 5.7 COP","Full load = 5.0 COP; Part load = 5.7 COP","Full load = 5.0 COP; Part load = 5.7 COP","Full load = 5.0 COP; Part load = 5.7 COP"]
[null,null,"Maximum external static pressure","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)","0.7 in. w.c. (175 Pa)"]
[null,null,"Maximum fan power","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)","0.4 W/cfm (0.85 W/L/s)"]
[null,null,"Water circulation pumps","VFD and NEMA premium efficiency","VFD and NEMA premium efficiency","VFD and NEMA premium efficiency","VFD and NEMA premium efficiency","VFD and NEMA premium efficiency","VFD and NEMA premium efficiency","VFD and NEMA premium efficiency","VFD and NEMA premium efficiency"]
[null,null,"Cooling tower/fluid cooler","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans","VFD on fans"]
[null,null,"Boiler efficiency","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec","90% Ec"]
[null,"Dedicated Outdoor Air System (DOAS)","Heating efficiency","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7"]
[null,null,"Cooling efficiency","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7","See Table 5-10 in HV7"]
[null,null,"Fan external static pressure","Constant volume = 1.0 in. w.c. (250 Pa); Variable volume (DCV) = 1.8 in. w.c. (450 Pa)","Constant volume = 1.0 in. w.c. (250 Pa); Variable volume (DCV) = 1.8 in. w.c. (450 Pa)","Constant volume = 1.0 in. w.c. (250 Pa); Variable volume (DCV) = 1.8 in. w.c. (450 Pa)","Constant volume = 1.0 in. w.c. (250 Pa); Variable volume (DCV) = 1.8 in. w.c. (450 Pa)","Constant volume = 1.0 in. w.c. (250 Pa); Variable volume (DCV) = 1.8 in. w.c. (450 Pa)","Constant volume = 1.0 in. w.c. (250 Pa); Variable volume (DCV) = 1.8 in. w.c. (450 Pa)","Constant volume = 1.0 in. w.c. (250 Pa); Variable volume (DCV) = 1.8 in. w.c. (450 Pa)","Constant volume = 1.0 in. w.c. (250 Pa); Variable volume (DCV) = 1.8 in. w.c. (450 Pa)"]
[null,null,"Fan and motor","65% mechanical/motor efficiency in absence of whole unit EER (COP) rating; Motor efficiency as per Standard 90.1-2010 Table 10.8B","65% mechanical/motor efficiency in absence of whole unit EER (COP) rating; Motor efficiency as per Standard 90.1-2010 Table 10.8B","65% mechanical/motor efficiency in absence of whole unit EER (COP) rating; Motor efficiency as per Standard 90.1-2010 Table 10.8B","65% mechanical/motor efficiency in absence of whole unit EER (COP) rating; Motor efficiency as per Standard 90.1-2010 Table 10.8B","65% mechanical/motor efficiency in absence of whole unit EER (COP) rating; Motor efficiency as per Standard 90.1-2010 Table 10.8B","65% mechanical/motor efficiency in absence of whole unit EER (COP) rating; Motor efficiency as per Standard 90.1-2010 Table 10.8B","65% mechanical/motor efficiency in absence of whole unit EER (COP) rating; Motor efficiency as per Standard 90.1-2010 Table 10.8B","65% mechanical/motor efficiency in absence of whole unit EER (COP) rating; Motor efficiency as per Standard 90.1-2010 Table 10.8B"]
[null,"Ventilation/Exhaust","Cooling capacity for which an economizer is required","No economizer","≥ 54,000 Btu/h (15.8 kW)","≥ 54,000 Btu/h (15.8 kW)","≥ 54,000 Btu/h (15.8 kW)","≥ 54,000 Btu/h (15.8 kW)","≥ 54,000 Btu/h (15.8 kW)","≥ 54,000 Btu/h (15.8 kW)","≥ 54,000 Btu/h (15.8 kW)"]
[null,null,"DCV/performance-based ventilation","Control ventilation air based on pollutant concentrations in space (CO2, VOCs, etc.)","Control ventilation air based on pollutant concentrations in space (CO2, VOCs, etc.)","Control ventilation air based on pollutant concentrations in space (CO2, VOCs, etc.)","Control ventilation air based on pollutant concentrations in space (CO2, VOCs, etc.)","Control ventilation air based on pollutant concentrations in space (CO2, VOCs, etc.)","Control ventilation air based on pollutant concentrations in space (CO2, VOCs, etc.)","Control ventilation air based on pollutant concentrations in space (CO2, VOCs, etc.)","Control ventilation air based on pollutant concentrations in space (CO2, VOCs, etc.)"]
[null,null,"Exhaust air recovery","A (humid) zones= 75% total effectiveness; B (dry) zones = 75% sensible effectiveness; Capture min. 80% available exhaust air, including general and bathroom, for energy recovery","A (humid) zones= 75% total effectiveness; B (dry) zones = 75% sensible effectiveness; Capture min. 80% available exhaust air, including general and bathroom, for energy recovery","A (humid) zones= 75% total effectiveness; B (dry) zones = 75% sensible effectiveness; Capture min. 80% available exhaust air, including general and bathroom, for energy recovery","A (humid) zones= 75% total effectiveness; B (dry) zones = 75% sensible effectiveness; Capture min. 80% available exhaust air, including general and bathroom, for energy recovery","A (humid) zones= 75% total effectiveness; B (dry) zones = 75% sensible effectiveness; Capture min. 80% available exhaust air, including general and bathroom, for energy recovery","A (humid) zones= 75% total effectiveness; B (dry) zones = 75% sensible effectiveness; Capture min. 80% available exhaust air, including general and bathroom, for energy recovery","A (humid) zones= 75% total effectiveness; B (dry) zones = 75% sensible effectiveness; Capture min. 80% available exhaust air, including general and bathroom, for energy recovery","A (humid) zones= 75% total effectiveness; B (dry) zones = 75% sensible effectiveness; Capture min. 80% available exhaust air, including general and bathroom, for energy recovery"]
[null,null,"Exhaust airflow control","Control based on occupancy using time clock or occupancy sensor","Control based on occupancy using time clock or occupancy sensor","Control based on occupancy using time clock or occupancy sensor","Control based on occupancy using time clock or occupancy sensor","Control based on occupancy using time clock or occupancy sensor","Control based on occupancy using time clock or occupancy sensor","Control based on occupancy using time clock or occupancy sensor","Control based on occupancy using time clock or occupancy sensor"]
[null,"Ducts and Dampers","Outdoor air damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper","Motorized damper"]
[null,null,"Duct seal class","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A","Seal class A"]
[null,null,"Insulation level","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)","R-6 (R-1.1)"]
[]
[null,"QA"]
[null,"Item","Component","AEDG Recommendation \nfor Zone 1","AEDG Recommendation \nfor Zone 2","AEDG Recommendation \nfor Zone 3","AEDG Recommendation \nfor Zone 4","AEDG Recommendation \nfor Zone 5","AEDG Recommendation \nfor Zone 6","AEDG Recommendation \nfor Zone 7","AEDG Recommendation \nfor Zone 8","Project Specification"]
[null,"M&V/Benchmarking","Electrical submeters","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heater, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heater, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heater, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heater, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heater, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heater, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heater, renewables, and whole building","Design and circuit for separate submeters for lighting, HVAC, general 120V, service water heater, renewables, and whole building"]
[null,null,"Benchmarks","Benchmark monthly energy use","Benchmark monthly energy use","Benchmark monthly energy use","Benchmark monthly energy use","Benchmark monthly energy use","Benchmark monthly energy use","Benchmark monthly energy use","Benchmark monthly energy use"]
[null,null,"Training","Facility operator or continuous benchmarking","Facility operator or continuous benchmarking","Facility operator or continuous benchmarking","Facility operator or continuous benchmarking","Facility operator or continuous benchmarking","Facility operator or continuous benchmarking","Facility operator or continuous benchmarking","Facility operator or continuous benchmarking"]